## README
SYNTHETIC DATA — 교육용 가상 데이터이며 실제 제품 사양·운영 기준과 무관합니다.

## product_master
product_code | product_name | family | family_name | description | standards | certifications | has_firmware | fw_latest | warranty_months | lifecycle_status | std_lead_time_weeks | moq | list_price_usd | weight_kg | dimensions_mm | ip_rating | operating_temp | tech_support_dept | doc_ids
MCCB-ABS-103c | MCCB 100AF | LV_BREAKER | Low-voltage circuit breakers | Molded case circuit breaker, 100A frame, thermal-magnetic trip unit | IEC 60947-2 | CE;CB;KC | N |  | 18 | ACTIVE | 4 | 10 | 85 | 0.9 | 75 x 130 x 60 | IP20 (front IP40) | -5 to +40 °C (derating above 40 °C) | TS_LV | DS-MCCB-ABS-103c;IG-MCCB-ABS-103c;TG-MCCB-ABS-103c;MG-MCCB-ABS-103c
MCCB-ABS-403c | MCCB 400AF | LV_BREAKER | Low-voltage circuit breakers | Molded case circuit breaker, 400A frame, adjustable thermal-magnetic trip unit | IEC 60947-2;UL 489 (-U variant) | CE;CB;KC;UL (-U variant) | N |  | 18 | ACTIVE | 5 | 5 | 420 | 5.2 | 140 x 257 x 109 | IP20 (front IP40) | -5 to +40 °C (derating above 40 °C) | TS_LV | DS-MCCB-ABS-403c;IG-MCCB-ABS-403c;TG-MCCB-ABS-403c;MG-MCCB-ABS-403c
ACB-AS-2000 | ACB 2000A | LV_BREAKER | Low-voltage circuit breakers | Air circuit breaker 2000A, draw-out type, electronic trip unit (LSIG) | IEC 60947-2 | CE;KC;CB | Y | 1.4 | 24 | ACTIVE | 8 | 1 | 6800 | 78 | 420 x 430 x 380 (draw-out) | IP31 (with door frame) | -5 to +55 °C | TS_LV | DS-ACB-AS-2000;IG-ACB-AS-2000;TG-ACB-AS-2000;RN-ACB-AS-2000
VCB-25kV-1250 | VCB 25.8kV 1250A | MV_EQUIP | MV breakers & switchgear | Vacuum circuit breaker 25.8kV / 1250A, spring operating mechanism | IEC 62271-100 | CE;KEMA type test report | N |  | 24 | ACTIVE | 12 | 1 | 14500 | 165 | 700 x 820 x 650 | IP4X (in panel) | -25 to +40 °C | TS_MV | DS-VCB-25kV-1250;IG-VCB-25kV-1250;TG-VCB-25kV-1250;MG-VCB-25kV-1250
ELCB-EBN-203c | ELCB 200AF | LV_BREAKER | Low-voltage circuit breakers | Earth leakage circuit breaker 200A frame, selectable sensitivity | IEC 60947-2 Annex B | CE;KC | N |  | 18 | ACTIVE | 4 | 5 | 310 | 2.6 | 105 x 165 x 86 | IP20 (front IP40) | -5 to +40 °C | TS_LV | DS-ELCB-EBN-203c;IG-ELCB-EBN-203c;TG-ELCB-EBN-203c;MG-ELCB-EBN-203c
CONT-MC-32a | Magnetic Contactor 32A | CONTROL | Motor control devices | Magnetic contactor 32A (AC-3), 3-pole, 1a1b auxiliary contacts | IEC 60947-4-1;UL 60947-4-1 | CE;UL;KC;CCC | N |  | 18 | ACTIVE | 3 | 20 | 38 | 0.5 | 45 x 82 x 95 | IP20 | -25 to +55 °C | TS_LV | DS-CONT-MC-32a;IG-CONT-MC-32a;TG-CONT-MC-32a;MG-CONT-MC-32a
RELAY-GMR-22 | Thermal Overload Relay 22A | CONTROL | Motor control devices | Thermal overload relay up to 22A, phase-loss sensitive, trip class 10A | IEC 60947-4-1 | CE;KC;UL | N |  | 18 | ACTIVE | 3 | 20 | 29 | 0.15 | 45 x 78 x 90 | IP20 | -25 to +55 °C (compensated) | TS_LV | DS-RELAY-GMR-22;IG-RELAY-GMR-22;TG-RELAY-GMR-22;MG-RELAY-GMR-22
INV-LSLV0075-S100 | LSLV S100 7.5kW VFD | DRIVE | Variable frequency drives | General purpose VFD 7.5kW, 3-phase 380-480V, sensorless vector | IEC 61800-5-1;IEC 61800-3 | CE;UL;KC | Y | 3.10 | 24 | ACTIVE | 4 | 1 | 980 | 3.6 | 150 x 284 x 156 | IP20 (IP66 option) | -10 to +50 °C (derating above 40 °C) | TS_AUTO | DS-INV-LSLV0075-S100;IG-INV-LSLV0075-S100;TG-INV-LSLV0075-S100;RN-INV-LSLV0075-S100
INV-LSLV0220-H100 | LSLV H100 22kW VFD | DRIVE | Variable frequency drives | HVAC / fan & pump VFD 22kW, built-in BACnet & Modbus, fire mode | IEC 61800-5-1;IEC 61800-3 | CE;UL;KC | Y | 2.40 | 24 | ACTIVE | 5 | 1 | 2350 | 10.5 | 200 x 380 x 220 | IP20 (IP54 option) | -10 to +50 °C | TS_AUTO | DS-INV-LSLV0220-H100;IG-INV-LSLV0220-H100;TG-INV-LSLV0220-H100;RN-INV-LSLV0220-H100
INV-LSLV0750-iS7 | iS7 75kW VFD | DRIVE | Variable frequency drives | High performance VFD 75kW, sensorless & sensored vector, built-in DC reactor | IEC 61800-5-1;IEC 61800-3 | CE;UL;KC | Y | 4.10 | 24 | MATURE | 6 | 1 | 7200 | 42 | 300 x 534 x 265 | IP21 | -10 to +50 °C | TS_AUTO | DS-INV-LSLV0750-iS7;IG-INV-LSLV0750-iS7;TG-INV-LSLV0750-iS7;RN-INV-LSLV0750-iS7
PLC-XGB-XBM-DR16S | XGB PLC CPU 16 I/O | PLC | Programmable logic controllers | Compact PLC CPU, 8 DC inputs / 8 relay outputs, modular expansion | IEC 61131-2 | CE;UL;KC | Y | 3.20 | 24 | ACTIVE | 3 | 1 | 260 | 0.3 | 30 x 90 x 64 | IP20 | 0 to +55 °C | TS_AUTO | DS-PLC-XGB-XBM-DR16S;IG-PLC-XGB-XBM-DR16S;TG-PLC-XGB-XBM-DR16S;RN-PLC-XGB-XBM-DR16S
PLC-XGI-CPUU | XGI PLC CPU Universal | PLC | Programmable logic controllers | High-performance IEC 61131-3 PLC CPU, built-in Ethernet | IEC 61131-2;IEC 61131-3 | CE;UL;KC | Y | 4.50 | 24 | ACTIVE | 4 | 1 | 1450 | 0.4 | 27 x 98 x 90 | IP20 | 0 to +55 °C | TS_AUTO | DS-PLC-XGI-CPUU;IG-PLC-XGI-CPUU;TG-PLC-XGI-CPUU;RN-PLC-XGI-CPUU
HMI-XGT-eXP60 | XGT Panel eXP60 (6") | HMI | Operator panels (HMI) | 6-inch TFT operator panel, 24VDC, Ethernet & serial | IEC 61131-2 | CE;KC | Y | 1.62 | 24 | MATURE | 4 | 1 | 520 | 0.9 | 184 x 140 x 52 | IP65 (front) | 0 to +50 °C | TS_AUTO | DS-HMI-XGT-eXP60;IG-HMI-XGT-eXP60;TG-HMI-XGT-eXP60;RN-HMI-XGT-eXP60
HMI-XGT-iXP90 | XGT iXP90 (10") | HMI | Operator panels (HMI) | 10.1-inch wide multi-touch operator panel, web server & VNC | IEC 61131-2 | CE;UL;KC | Y | 2.08 | 24 | ACTIVE | 4 | 1 | 1380 | 1.8 | 272 x 191 x 59 | IP66 (front) | 0 to +50 °C | TS_AUTO | DS-HMI-XGT-iXP90;IG-HMI-XGT-iXP90;TG-HMI-XGT-iXP90;RN-HMI-XGT-iXP90
TRF-DRY-630 | Cast Resin Dry-Type TRF 630kVA | TRANSFORMER | Power transformers | Cast resin dry-type transformer 630kVA, 11/0.415kV, Dyn11, AN/AF | IEC 60076-11 | Type test report (IEC 60076-11);KC | N |  | 24 | ACTIVE | 10 | 1 | 16800 | 1850 | 1500 x 900 x 1650 | IP00 (IP21/IP23 enclosure option) | -25 to +40 °C | TS_TRF | DS-TRF-DRY-630;IG-TRF-DRY-630;TG-TRF-DRY-630;MG-TRF-DRY-630
TRF-OIL-1000 | Oil-immersed Transformer 1000kVA | TRANSFORMER | Power transformers | Oil-immersed transformer 1000kVA, 11/0.433kV, ONAN, conservator type | IEC 60076-1;IEC 60076-2 | Type test report (IEC 60076);KC | N |  | 24 | ACTIVE | 12 | 1 | 21500 | 3200 | 1900 x 1300 x 2000 | IP54 (outdoor) | -25 to +40 °C | TS_TRF | DS-TRF-OIL-1000;IG-TRF-OIL-1000;TG-TRF-OIL-1000;MG-TRF-OIL-1000
METER-LP3500-3P4W | Smart Power Meter 3P4W | METER | Power & energy meters | Panel-mount multifunction power meter, class 0.5S, harmonics & logging | IEC 62053-22;IEC 61557-12 | CE;KC | Y | 1.80 | 24 | ACTIVE | 3 | 5 | 340 | 0.45 | 96 x 96 x 70 | IP54 (front) | -10 to +55 °C | TS_LV | DS-METER-LP3500-3P4W;IG-METER-LP3500-3P4W;TG-METER-LP3500-3P4W;RN-METER-LP3500-3P4W
METER-LPB-DIN | DIN Rail Energy Meter | METER | Power & energy meters | DIN-rail direct-connected energy meter up to 80A, MID class B | IEC 62053-21;EN 50470-3 | CE;MID | N |  | 24 | ACTIVE | 3 | 10 | 95 | 0.4 | 72 x 90 x 66 (4 modules) | IP51 (front) | -25 to +55 °C | TS_LV | DS-METER-LPB-DIN;IG-METER-LPB-DIN;TG-METER-LPB-DIN;MG-METER-LPB-DIN
ESS-PCS-100kW | ESS PCS 100kW | ESS | Energy storage systems | Bidirectional power conversion system 100kW for battery energy storage | IEC 62477-1;IEC 62116;IEC 61000-6-2/-4 | CE;KC;UL 1741 SB (-U variant) | Y | 2.70 | 36 | ACTIVE | 10 | 1 | 26000 | 520 | 1000 x 800 x 2000 | IP54 | -20 to +50 °C (derating above 45 °C) | TS_ENERGY | DS-ESS-PCS-100kW;IG-ESS-PCS-100kW;TG-ESS-PCS-100kW;RN-ESS-PCS-100kW
ESS-BMS-V3 | ESS BMS Controller V3 | ESS | Energy storage systems | Rack-level battery management system controller for LFP racks | IEC 62619;UL 1973 (component) | CE;KC | Y | 3.50 | 36 | ACTIVE | 8 | 1 | 3900 | 6 | 482 x 132 x 400 (19" 3U) | IP20 | -10 to +50 °C | TS_ENERGY | DS-ESS-BMS-V3;IG-ESS-BMS-V3;TG-ESS-BMS-V3;RN-ESS-BMS-V3
PV-INV-SOLAR-25 | Solar Inverter 25kW | PV | PV inverters | Three-phase string PV inverter 25kW, 3 MPPT | IEC 62109-1;IEC 62109-2;IEC 61727;IEC 62116 | CE;VDE-AR-N 4105;KC | Y | 1.90 | 60 | ACTIVE | 6 | 1 | 2900 | 36 | 580 x 520 x 230 | IP66 | -25 to +60 °C (derating above 45 °C) | TS_ENERGY | DS-PV-INV-SOLAR-25;IG-PV-INV-SOLAR-25;TG-PV-INV-SOLAR-25;RN-PV-INV-SOLAR-25
SWGR-MV-12kV | MV Switchgear Panel 12kV | MV_EQUIP | MV breakers & switchgear | 12kV air-insulated metal-clad switchgear, withdrawable VCB | IEC 62271-200 | KEMA type test report;CE | N |  | 24 | ACTIVE | 14 | 1 | 32000 | 1100 | 800 x 1500 x 2300 (per panel) | IP4X | -5 to +40 °C | TS_MV | DS-SWGR-MV-12kV;IG-SWGR-MV-12kV;TG-SWGR-MV-12kV;MG-SWGR-MV-12kV
UPS-LSU-10K | Online UPS 10kVA | UPS | Uninterruptible power supplies | Online double-conversion UPS 10kVA/9kW, single-phase | IEC 62040-1;IEC 62040-3 | CE;KC | Y | 2.30 | 24 | MATURE | 4 | 1 | 2600 | 28 | 190 x 450 x 690 | IP20 | 0 to +40 °C | TS_ENERGY | DS-UPS-LSU-10K;IG-UPS-LSU-10K;TG-UPS-LSU-10K;RN-UPS-LSU-10K

## product_spec_facts
product_code | attribute | value | doc_id | section
MCCB-ABS-103c | Frame size | 100AF | DS-MCCB-ABS-103c | 2.1
MCCB-ABS-103c | Rated current (In) | 15, 20, 30, 40, 50, 60, 75, 100 A | DS-MCCB-ABS-103c | 2.1
MCCB-ABS-103c | Rated operational voltage (Ue) | AC 690 V max | DS-MCCB-ABS-103c | 2.1
MCCB-ABS-103c | Ultimate breaking capacity Icu at AC 415 V | 37 kA | DS-MCCB-ABS-103c | 2.2
MCCB-ABS-103c | Service breaking capacity Ics | 75% of Icu | DS-MCCB-ABS-103c | 2.2
MCCB-ABS-103c | Number of poles | 2P / 3P / 4P | DS-MCCB-ABS-103c | 2.1
MCCB-ABS-103c | Mechanical endurance | 8,500 operations | DS-MCCB-ABS-103c | 2.3
MCCB-ABS-103c | Electrical endurance | 1,500 operations at In | DS-MCCB-ABS-103c | 2.3
MCCB-ABS-103c | Terminal tightening torque | 3.5 N·m (M5) | DS-MCCB-ABS-103c | 3.1
MCCB-ABS-103c | Magnetic trip setting | Fixed, 10 x In | DS-MCCB-ABS-103c | 2.4
MCCB-ABS-403c | Frame size | 400AF | DS-MCCB-ABS-403c | 2.1
MCCB-ABS-403c | Rated current (In) | 250, 300, 350, 400 A | DS-MCCB-ABS-403c | 2.1
MCCB-ABS-403c | Ultimate breaking capacity Icu at AC 415 V | 50 kA | DS-MCCB-ABS-403c | 2.2
MCCB-ABS-403c | Service breaking capacity Ics | 100% of Icu | DS-MCCB-ABS-403c | 2.2
MCCB-ABS-403c | Thermal trip adjustment | 0.8 to 1.0 x In | DS-MCCB-ABS-403c | 2.4
MCCB-ABS-403c | Magnetic trip adjustment | 5 to 10 x In | DS-MCCB-ABS-403c | 2.4
MCCB-ABS-403c | Mechanical endurance | 7,000 operations | DS-MCCB-ABS-403c | 2.3
MCCB-ABS-403c | Terminal tightening torque | 18 N·m (M10) | DS-MCCB-ABS-403c | 3.1
MCCB-ABS-403c | UL 489 interrupting rating at 480 V (-U variant) | 35 kA | DS-MCCB-ABS-403c | 2.2
ACB-AS-2000 | Rated current (In) | 2000 A | DS-ACB-AS-2000 | 2.1
ACB-AS-2000 | Ultimate breaking capacity Icu at AC 415 V | 85 kA | DS-ACB-AS-2000 | 2.2
ACB-AS-2000 | Short-time withstand current Icw (1 s) | 65 kA | DS-ACB-AS-2000 | 2.2
ACB-AS-2000 | Trip unit protection functions | L (long-time), S (short-time), I (instantaneous), G (ground fault) | DS-ACB-AS-2000 | 2.4
ACB-AS-2000 | Motor operator control voltage | AC/DC 110-240 V | DS-ACB-AS-2000 | 2.5
ACB-AS-2000 | Closing time | ≤ 70 ms | DS-ACB-AS-2000 | 2.3
ACB-AS-2000 | Mechanical endurance (with maintenance) | 20,000 operations | DS-ACB-AS-2000 | 2.3
ACB-AS-2000 | Trip unit communication | Modbus RTU (RS-485) | DS-ACB-AS-2000 | 2.5
VCB-25kV-1250 | Rated voltage | 25.8 kV | DS-VCB-25kV-1250 | 2.1
VCB-25kV-1250 | Rated normal current | 1250 A | DS-VCB-25kV-1250 | 2.1
VCB-25kV-1250 | Rated short-circuit breaking current | 25 kA | DS-VCB-25kV-1250 | 2.2
VCB-25kV-1250 | Rated short-time withstand | 25 kA / 3 s | DS-VCB-25kV-1250 | 2.2
VCB-25kV-1250 | Lightning impulse withstand (BIL) | 125 kV | DS-VCB-25kV-1250 | 2.2
VCB-25kV-1250 | Mechanical endurance class | M2 (10,000 operations) | DS-VCB-25kV-1250 | 2.3
VCB-25kV-1250 | Electrical endurance class | E2 | DS-VCB-25kV-1250 | 2.3
VCB-25kV-1250 | Spring charging motor voltage | DC 110 V / DC 125 V / AC 220 V | DS-VCB-25kV-1250 | 2.4
ELCB-EBN-203c | Rated current (In) | 125, 150, 175, 200 A | DS-ELCB-EBN-203c | 2.1
ELCB-EBN-203c | Rated residual operating current IΔn | 30 / 100 / 300 / 500 mA selectable | DS-ELCB-EBN-203c | 2.4
ELCB-EBN-203c | Residual current type | Type AC (Type A optional) | DS-ELCB-EBN-203c | 2.4
ELCB-EBN-203c | Operating time at IΔn | ≤ 0.1 s (instantaneous setting) | DS-ELCB-EBN-203c | 2.4
ELCB-EBN-203c | Ultimate breaking capacity Icu at AC 415 V | 37 kA | DS-ELCB-EBN-203c | 2.2
ELCB-EBN-203c | Test button operating voltage range | AC 200-460 V | DS-ELCB-EBN-203c | 2.4
CONT-MC-32a | Rated operational current AC-3 at 400 V | 32 A | DS-CONT-MC-32a | 2.1
CONT-MC-32a | Motor power AC-3 at 400 V | 15 kW | DS-CONT-MC-32a | 2.1
CONT-MC-32a | Coil voltage options | AC 24/48/110/220/380/440 V, DC 24/48/110/220 V | DS-CONT-MC-32a | 2.2
CONT-MC-32a | Coil pick-up voltage | 80-110% of rated coil voltage | DS-CONT-MC-32a | 2.2
CONT-MC-32a | Mechanical endurance | 10 million operations | DS-CONT-MC-32a | 2.3
CONT-MC-32a | Electrical endurance AC-3 | 1.2 million operations | DS-CONT-MC-32a | 2.3
CONT-MC-32a | Auxiliary contacts | 1a1b built-in | DS-CONT-MC-32a | 2.1
RELAY-GMR-22 | Current setting ranges | 0.1-0.16 A up to 16-22 A (13 ranges) | DS-RELAY-GMR-22 | 2.1
RELAY-GMR-22 | Trip class | Class 10A | DS-RELAY-GMR-22 | 2.1
RELAY-GMR-22 | Phase-loss sensitivity | Yes (differential mechanism) | DS-RELAY-GMR-22 | 2.1
RELAY-GMR-22 | Reset mode | Manual / automatic selectable | DS-RELAY-GMR-22 | 2.2
RELAY-GMR-22 | Ambient temperature compensation | -25 to +55 °C | DS-RELAY-GMR-22 | 2.2
INV-LSLV0075-S100 | Rated output (heavy duty) | 7.5 kW / 16 A | DS-INV-LSLV0075-S100 | 2.1
INV-LSLV0075-S100 | Input voltage | 3-phase AC 380-480 V (-15% to +10%), 50/60 Hz | DS-INV-LSLV0075-S100 | 2.1
INV-LSLV0075-S100 | Overload capacity (heavy duty) | 150% for 1 minute | DS-INV-LSLV0075-S100 | 2.1
INV-LSLV0075-S100 | Control method | V/F, slip compensation, sensorless vector | DS-INV-LSLV0075-S100 | 2.2
INV-LSLV0075-S100 | Output frequency range | 0.01-400 Hz | DS-INV-LSLV0075-S100 | 2.2
INV-LSLV0075-S100 | Built-in communication | RS-485 Modbus RTU / LS INV protocol | DS-INV-LSLV0075-S100 | 2.3
INV-LSLV0075-S100 | Safe Torque Off | STO, SIL3 / PLe | DS-INV-LSLV0075-S100 | 2.4
INV-LSLV0075-S100 | Built-in EMC filter | Category C3 | DS-INV-LSLV0075-S100 | 2.4
INV-LSLV0075-S100 | Braking | Built-in braking transistor (external resistor) | DS-INV-LSLV0075-S100 | 2.4
INV-LSLV0220-H100 | Rated output (normal duty) | 22 kW / 45 A | DS-INV-LSLV0220-H100 | 2.1
INV-LSLV0220-H100 | Overload capacity (normal duty) | 120% for 1 minute | DS-INV-LSLV0220-H100 | 2.1
INV-LSLV0220-H100 | Built-in communication | BACnet MS/TP, Modbus RTU, Metasys N2 | DS-INV-LSLV0220-H100 | 2.3
INV-LSLV0220-H100 | Fire mode | Yes (fault-ignore run, logged) | DS-INV-LSLV0220-H100 | 2.2
INV-LSLV0220-H100 | PID controllers | Main PID + 2 external PID | DS-INV-LSLV0220-H100 | 2.2
INV-LSLV0220-H100 | Multi-motor control | Up to 5 pumps (MMC) | DS-INV-LSLV0220-H100 | 2.2
INV-LSLV0220-H100 | Built-in DC reactor | Yes | DS-INV-LSLV0220-H100 | 2.4
INV-LSLV0750-iS7 | Rated output (heavy duty) | 75 kW / 150 A | DS-INV-LSLV0750-iS7 | 2.1
INV-LSLV0750-iS7 | Overload capacity (heavy duty) | 150% for 1 minute | DS-INV-LSLV0750-iS7 | 2.1
INV-LSLV0750-iS7 | Control method | V/F, sensorless vector, sensored vector (encoder option) | DS-INV-LSLV0750-iS7 | 2.2
INV-LSLV0750-iS7 | Communication options | Profibus-DP, EtherNet/IP, Modbus TCP, CANopen | DS-INV-LSLV0750-iS7 | 2.3
INV-LSLV0750-iS7 | Built-in DC reactor | Yes | DS-INV-LSLV0750-iS7 | 2.4
INV-LSLV0750-iS7 | Encoder option input | Line driver / open collector, up to 200 kHz | DS-INV-LSLV0750-iS7 | 2.3
PLC-XGB-XBM-DR16S | Built-in I/O | 8 DC inputs (24 V) / 8 relay outputs | DS-PLC-XGB-XBM-DR16S | 2.1
PLC-XGB-XBM-DR16S | Program capacity | 20 k steps | DS-PLC-XGB-XBM-DR16S | 2.2
PLC-XGB-XBM-DR16S | Processing speed | 0.16 µs/step (basic instruction) | DS-PLC-XGB-XBM-DR16S | 2.2
PLC-XGB-XBM-DR16S | Max expansion modules | 7 modules | DS-PLC-XGB-XBM-DR16S | 2.1
PLC-XGB-XBM-DR16S | Built-in communication | RS-232C 1 ch + RS-485 1 ch | DS-PLC-XGB-XBM-DR16S | 2.3
PLC-XGB-XBM-DR16S | Relay output rating | AC 250 V / DC 24 V, 2 A per point | DS-PLC-XGB-XBM-DR16S | 2.1
PLC-XGB-XBM-DR16S | Backup battery life | Approx. 5 years (lithium) | DS-PLC-XGB-XBM-DR16S | 2.4
PLC-XGI-CPUU | Programming languages | LD, ST, SFC, FBD, IL (IEC 61131-3) | DS-PLC-XGI-CPUU | 2.2
PLC-XGI-CPUU | Program memory | 1 MB | DS-PLC-XGI-CPUU | 2.2
PLC-XGI-CPUU | Processing speed | 8.5 ns/step (LD basic) | DS-PLC-XGI-CPUU | 2.2
PLC-XGI-CPUU | Max local I/O points | 6,144 points | DS-PLC-XGI-CPUU | 2.1
PLC-XGI-CPUU | Built-in Ethernet | 1 port, 100 Mbps, Modbus TCP server/client | DS-PLC-XGI-CPUU | 2.3
PLC-XGI-CPUU | Max expansion bases | 7 bases | DS-PLC-XGI-CPUU | 2.1
HMI-XGT-eXP60 | Display | 6-inch TFT, 800 x 480, 65k colors | DS-HMI-XGT-eXP60 | 2.1
HMI-XGT-eXP60 | Power supply | DC 24 V (19.2-28.8 V) | DS-HMI-XGT-eXP60 | 2.1
HMI-XGT-eXP60 | Interfaces | Ethernet 1 port, RS-232C, RS-422/485, USB host | DS-HMI-XGT-eXP60 | 2.3
HMI-XGT-eXP60 | Front protection | IP65 | DS-HMI-XGT-eXP60 | 2.1
HMI-XGT-eXP60 | User memory | 64 MB | DS-HMI-XGT-eXP60 | 2.2
HMI-XGT-eXP60 | Backlight life | Approx. 50,000 hours | DS-HMI-XGT-eXP60 | 2.1
HMI-XGT-iXP90 | Display | 10.1-inch TFT, 1280 x 800, multi-touch | DS-HMI-XGT-iXP90 | 2.1
HMI-XGT-iXP90 | Processor | Quad-core 1.0 GHz | DS-HMI-XGT-iXP90 | 2.2
HMI-XGT-iXP90 | Remote access | Web server, VNC server | DS-HMI-XGT-iXP90 | 2.3
HMI-XGT-iXP90 | Interfaces | Ethernet 2 ports, RS-232C, RS-422/485, USB host 2 | DS-HMI-XGT-iXP90 | 2.3
HMI-XGT-iXP90 | Front protection | IP66 | DS-HMI-XGT-iXP90 | 2.1
HMI-XGT-iXP90 | Power consumption | Max 18 W | DS-HMI-XGT-iXP90 | 2.1
TRF-DRY-630 | Rated power | 630 kVA (AN) / 880 kVA (AF, with fans) | DS-TRF-DRY-630 | 2.1
TRF-DRY-630 | Voltage ratio | 11 kV / 0.415 kV | DS-TRF-DRY-630 | 2.1
TRF-DRY-630 | Vector group | Dyn11 | DS-TRF-DRY-630 | 2.1
TRF-DRY-630 | Impedance voltage | 6% at 120 °C | DS-TRF-DRY-630 | 2.2
TRF-DRY-630 | Off-circuit tap range | ±2 x 2.5% | DS-TRF-DRY-630 | 2.2
TRF-DRY-630 | Insulation class / temperature rise | Class F / 100 K | DS-TRF-DRY-630 | 2.2
TRF-DRY-630 | No-load loss | 1,300 W | DS-TRF-DRY-630 | 2.3
TRF-DRY-630 | Load loss at 120 °C | 6,500 W | DS-TRF-DRY-630 | 2.3
TRF-DRY-630 | Environmental / climatic / fire class | E2 / C2 / F1 | DS-TRF-DRY-630 | 2.4
TRF-DRY-630 | Winding temperature alarm / trip | 140 °C / 155 °C (PT100) | DS-TRF-DRY-630 | 2.5
TRF-OIL-1000 | Rated power | 1000 kVA (ONAN) | DS-TRF-OIL-1000 | 2.1
TRF-OIL-1000 | Voltage ratio | 11 kV / 0.433 kV | DS-TRF-OIL-1000 | 2.1
TRF-OIL-1000 | Vector group | Dyn11 | DS-TRF-OIL-1000 | 2.1
TRF-OIL-1000 | Impedance voltage | 5% at 75 °C | DS-TRF-OIL-1000 | 2.2
TRF-OIL-1000 | Off-circuit tap range | ±2 x 2.5% | DS-TRF-OIL-1000 | 2.2
TRF-OIL-1000 | Insulating liquid | Mineral oil (IEC 60296) | DS-TRF-OIL-1000 | 2.2
TRF-OIL-1000 | Top-oil temperature alarm / trip | 90 °C / 100 °C | DS-TRF-OIL-1000 | 2.5
TRF-OIL-1000 | Protection devices | Buchholz relay, pressure relief device, oil & winding temperature indicators | DS-TRF-OIL-1000 | 2.5
TRF-OIL-1000 | No-load loss | 1,100 W | DS-TRF-OIL-1000 | 2.3
TRF-OIL-1000 | Load loss at 75 °C | 9,500 W | DS-TRF-OIL-1000 | 2.3
METER-LP3500-3P4W | Accuracy class (active energy) | Class 0.5S (IEC 62053-22) | DS-METER-LP3500-3P4W | 2.1
METER-LP3500-3P4W | Voltage input | 3P4W 57.7-400 V L-N | DS-METER-LP3500-3P4W | 2.1
METER-LP3500-3P4W | Current input | CT secondary 5 A or 1 A | DS-METER-LP3500-3P4W | 2.1
METER-LP3500-3P4W | Communication | Modbus RTU (RS-485), Modbus TCP option | DS-METER-LP3500-3P4W | 2.3
METER-LP3500-3P4W | Harmonic measurement | Up to 31st order | DS-METER-LP3500-3P4W | 2.2
METER-LP3500-3P4W | Data logging memory | 8 MB (approx. 1 year at 15-min interval) | DS-METER-LP3500-3P4W | 2.2
METER-LP3500-3P4W | Auxiliary supply | AC/DC 85-265 V | DS-METER-LP3500-3P4W | 2.1
METER-LPB-DIN | Accuracy class | Class 1 (IEC 62053-21) / MID class B | DS-METER-LPB-DIN | 2.1
METER-LPB-DIN | Maximum current (direct connection) | 80 A | DS-METER-LPB-DIN | 2.1
METER-LPB-DIN | Wiring | 1P2W or 3P4W (model dependent) | DS-METER-LPB-DIN | 2.1
METER-LPB-DIN | Communication | Modbus RTU (RS-485) | DS-METER-LPB-DIN | 2.3
METER-LPB-DIN | Pulse output | Open collector, 1000 imp/kWh | DS-METER-LPB-DIN | 2.3
ESS-PCS-100kW | Rated AC power | 100 kW | DS-ESS-PCS-100kW | 2.1
ESS-PCS-100kW | AC grid connection | 3-phase 400 V, 50/60 Hz | DS-ESS-PCS-100kW | 2.1
ESS-PCS-100kW | DC voltage range | 600-900 V | DS-ESS-PCS-100kW | 2.1
ESS-PCS-100kW | Max efficiency | 97.5% | DS-ESS-PCS-100kW | 2.2
ESS-PCS-100kW | Battery interface | CAN 2.0B to BMS | DS-ESS-PCS-100kW | 2.3
ESS-PCS-100kW | SCADA interface | Modbus TCP | DS-ESS-PCS-100kW | 2.3
ESS-PCS-100kW | Anti-islanding | IEC 62116 compliant | DS-ESS-PCS-100kW | 2.4
ESS-PCS-100kW | Grid code profiles | Selectable country profiles (parameter G-01) | DS-ESS-PCS-100kW | 2.4
ESS-BMS-V3 | Cell chemistry | LFP | DS-ESS-BMS-V3 | 2.1
ESS-BMS-V3 | Cells monitored per rack | Up to 240 cells in series | DS-ESS-BMS-V3 | 2.1
ESS-BMS-V3 | Cell voltage accuracy | ±5 mV | DS-ESS-BMS-V3 | 2.2
ESS-BMS-V3 | SOC estimation accuracy | ±3% | DS-ESS-BMS-V3 | 2.2
ESS-BMS-V3 | Communication | CAN 2.0B (PCS), Modbus TCP (EMS) | DS-ESS-BMS-V3 | 2.3
ESS-BMS-V3 | Cell over-voltage protection (default) | 3.65 V | DS-ESS-BMS-V3 | 2.4
ESS-BMS-V3 | Cell over-temperature protection (default) | 55 °C | DS-ESS-BMS-V3 | 2.4
PV-INV-SOLAR-25 | Rated AC output | 25 kW | DS-PV-INV-SOLAR-25 | 2.1
PV-INV-SOLAR-25 | Max DC input voltage | 1100 V | DS-PV-INV-SOLAR-25 | 2.1
PV-INV-SOLAR-25 | MPPT voltage range | 200-1000 V | DS-PV-INV-SOLAR-25 | 2.1
PV-INV-SOLAR-25 | Number of MPPT / strings | 3 MPPT / 2 strings each | DS-PV-INV-SOLAR-25 | 2.1
PV-INV-SOLAR-25 | Max efficiency | 98.6% | DS-PV-INV-SOLAR-25 | 2.2
PV-INV-SOLAR-25 | Protection degree | IP66 | DS-PV-INV-SOLAR-25 | 2.4
PV-INV-SOLAR-25 | Insulation resistance threshold (default) | 100 kΩ | DS-PV-INV-SOLAR-25 | 2.4
PV-INV-SOLAR-25 | Communication | RS-485 Modbus, Wi-Fi dongle option | DS-PV-INV-SOLAR-25 | 2.3
SWGR-MV-12kV | Rated voltage | 12 kV | DS-SWGR-MV-12kV | 2.1
SWGR-MV-12kV | Rated busbar current | 1250 A (up to 2500 A) | DS-SWGR-MV-12kV | 2.1
SWGR-MV-12kV | Rated short-time withstand | 25 kA / 3 s | DS-SWGR-MV-12kV | 2.2
SWGR-MV-12kV | Internal arc classification | IAC AFLR 25 kA 1 s | DS-SWGR-MV-12kV | 2.2
SWGR-MV-12kV | Loss of service continuity | LSC2B-PM | DS-SWGR-MV-12kV | 2.2
SWGR-MV-12kV | Power frequency withstand | 28 kV / 1 min | DS-SWGR-MV-12kV | 2.2
SWGR-MV-12kV | Lightning impulse withstand | 75 kV | DS-SWGR-MV-12kV | 2.2
UPS-LSU-10K | Rated power | 10 kVA / 9 kW | DS-UPS-LSU-10K | 2.1
UPS-LSU-10K | Input / output | 1-phase 220/230/240 V, 50/60 Hz | DS-UPS-LSU-10K | 2.1
UPS-LSU-10K | Efficiency (online mode) | 94% | DS-UPS-LSU-10K | 2.2
UPS-LSU-10K | Transfer time (mains to battery) | 0 ms | DS-UPS-LSU-10K | 2.2
UPS-LSU-10K | Battery | External, 16 x 12 V (192 V DC) | DS-UPS-LSU-10K | 2.1
UPS-LSU-10K | Communication | RS-232, USB, SNMP card slot | DS-UPS-LSU-10K | 2.3
UPS-LSU-10K | Input voltage window (default) | 176-276 V at full load | DS-UPS-LSU-10K | 2.2

## firmware_history
product_code | fw_version | release_date | is_latest | changes | doc_id
ACB-AS-2000 | 1.2 | 2024-11-04 | N | Initial release of trip unit firmware for AS series | RN-ACB-AS-2000
ACB-AS-2000 | 1.3 | 2025-06-16 | N | Fixed: ground fault (G) pickup delay ignored when set to 0.1 s ¦ Added: Modbus register for contact wear percentage | RN-ACB-AS-2000
ACB-AS-2000 | 1.4 | 2026-03-09 | Y | Fixed: false T.SF self-diagnosis alarm after control power dip below 85 V ¦ Improved: event log capacity from 64 to 256 entries | RN-ACB-AS-2000
INV-LSLV0075-S100 | 3.00 | 2024-09-02 | N | Baseline release | RN-INV-LSLV0075-S100
INV-LSLV0075-S100 | 3.05 | 2025-04-21 | N | Fixed: Modbus RTU response timeout when polling interval < 20 ms (E.CO) ¦ Added: parameter copy compatibility check on keypad | RN-INV-LSLV0075-S100
INV-LSLV0075-S100 | 3.10 | 2026-01-12 | Y | Fixed: E.EP parameter write error when copying from 3.00 keypad ¦ Improved: stall prevention during fast acceleration ¦ Added: fan run-hour counter (monitor parameter) | RN-INV-LSLV0075-S100
INV-LSLV0220-H100 | 2.20 | 2024-10-14 | N | Baseline release | RN-INV-LSLV0220-H100
INV-LSLV0220-H100 | 2.31 | 2025-05-26 | N | Fixed: BACnet MS/TP token loss on networks with > 32 nodes (E.CO) ¦ Added: pump clean function | RN-INV-LSLV0220-H100
INV-LSLV0220-H100 | 2.40 | 2026-02-02 | Y | Fixed: MMC auxiliary motor not staging when PID feedback noisy ¦ Improved: fire mode event log with timestamp | RN-INV-LSLV0220-H100
INV-LSLV0750-iS7 | 4.00 | 2024-08-19 | N | Baseline release | RN-INV-LSLV0750-iS7
INV-LSLV0750-iS7 | 4.05 | 2025-03-10 | N | Fixed: E.OC trip at restart after momentary power loss (speed search) | RN-INV-LSLV0750-iS7
INV-LSLV0750-iS7 | 4.10 | 2025-12-15 | Y | Fixed: EtherNet/IP option loses connection after 49.7 days uptime ¦ Added: cooling fan life warning | RN-INV-LSLV0750-iS7
PLC-XGB-XBM-DR16S | 3.00 | 2024-07-01 | N | Baseline release | RN-PLC-XGB-XBM-DR16S
PLC-XGB-XBM-DR16S | 3.10 | 2025-02-17 | N | Fixed: P.04 program checksum error after repeated power cycling within 1 s | RN-PLC-XGB-XBM-DR16S
PLC-XGB-XBM-DR16S | 3.20 | 2025-11-03 | Y | Added: Modbus RTU master up to 64 blocks ¦ Fixed: RTC drift > 30 s/month at high ambient temperature | RN-PLC-XGB-XBM-DR16S
PLC-XGI-CPUU | 4.20 | 2024-09-23 | N | Baseline release | RN-PLC-XGI-CPUU
PLC-XGI-CPUU | 4.40 | 2025-06-02 | N | Fixed: P.05 Ethernet timeout under broadcast storm > 2,000 frames/s | RN-PLC-XGI-CPUU
PLC-XGI-CPUU | 4.50 | 2026-02-23 | Y | Added: online change for structured data types ¦ Fixed: watchdog false trip during online change of large FB | RN-PLC-XGI-CPUU
HMI-XGT-eXP60 | 1.50 | 2024-06-10 | N | Baseline OS | RN-HMI-XGT-eXP60
HMI-XGT-eXP60 | 1.58 | 2025-03-24 | N | Fixed: screen freeze after ~30 days continuous uptime | RN-HMI-XGT-eXP60
HMI-XGT-eXP60 | 1.62 | 2025-10-20 | Y | Fixed: H.03 project download failure with editor 3.2 or later ¦ Added: alarm history export to USB as CSV | RN-HMI-XGT-eXP60
HMI-XGT-iXP90 | 2.00 | 2024-10-07 | N | Baseline OS | RN-HMI-XGT-iXP90
HMI-XGT-iXP90 | 2.05 | 2025-05-12 | N | Fixed: H.02 PLC communication timeout when two Ethernet ports on same subnet | RN-HMI-XGT-iXP90
HMI-XGT-iXP90 | 2.08 | 2026-01-26 | Y | Fixed: touch drift after warm restart ¦ Added: TLS 1.3 for web server | RN-HMI-XGT-iXP90
METER-LP3500-3P4W | 1.60 | 2024-08-05 | N | Baseline release | RN-METER-LP3500-3P4W
METER-LP3500-3P4W | 1.72 | 2025-04-07 | N | Fixed: energy register reset after power loss during flash write | RN-METER-LP3500-3P4W
METER-LP3500-3P4W | 1.80 | 2025-12-01 | Y | Added: Modbus TCP gateway mode ¦ Fixed: R.01 no response when baud 38400 and parity even | RN-METER-LP3500-3P4W
ESS-PCS-100kW | 2.50 | 2024-11-11 | N | Baseline release | RN-ESS-PCS-100kW
ESS-PCS-100kW | 2.62 | 2025-07-07 | N | Fixed: G.06 BMS communication loss with BMS FW 3.4 heartbeat change | RN-ESS-PCS-100kW
ESS-PCS-100kW | 2.70 | 2026-03-30 | Y | Added: frequency-watt response curve for new grid codes ¦ Fixed: G.02 nuisance trip on ROCOF measurement during genset operation | RN-ESS-PCS-100kW
ESS-BMS-V3 | 3.30 | 2024-10-28 | N | Baseline release | RN-ESS-BMS-V3
ESS-BMS-V3 | 3.40 | 2025-05-19 | N | Changed: CAN heartbeat period from 100 ms to 200 ms ¦ Improved: passive balancing threshold 30 mV → 20 mV | RN-ESS-BMS-V3
ESS-BMS-V3 | 3.50 | 2026-01-19 | Y | Fixed: SOC jump of up to 15% after long rest period ¦ Fixed: contactor status mismatch alarm on cold start | RN-ESS-BMS-V3
PV-INV-SOLAR-25 | 1.70 | 2024-09-09 | N | Baseline release | RN-PV-INV-SOLAR-25
PV-INV-SOLAR-25 | 1.82 | 2025-04-14 | N | Fixed: S.01 false insulation fault at sunrise with humidity > 95% | RN-PV-INV-SOLAR-25
PV-INV-SOLAR-25 | 1.90 | 2025-12-08 | Y | Added: reactive power Q(U) curve ¦ Fixed: Wi-Fi dongle reconnect failure after router reboot | RN-PV-INV-SOLAR-25
UPS-LSU-10K | 2.10 | 2024-07-15 | N | Baseline release | RN-UPS-LSU-10K
UPS-LSU-10K | 2.20 | 2025-03-03 | N | Added: generator mode with wider frequency window (45-65 Hz) | RN-UPS-LSU-10K
UPS-LSU-10K | 2.30 | 2025-11-17 | Y | Fixed: SNMP card not detected after hot-swap ¦ Fixed: battery test result not logged when load < 10% | RN-UPS-LSU-10K

## fault_catalog
fault_id | family | applies_to | error_code | symptom | root_cause | diagnosis | action | severity_hint | needs_onsite | needs_rma | replacement_part | fw_fix_version | typical_resolution_hours
FLT-001 | DRIVE | INV-LSLV0075-S100;INV-LSLV0220-H100;INV-LSLV0750-iS7 | E.OC | Over-current trip during acceleration | Acceleration time too short for load inertia | Check trip log: output current at trip > 200% of rated during ACC | Increase acceleration time and enable stall prevention | P2 | N | N |  |  | 6
FLT-002 | DRIVE | INV-LSLV0075-S100;INV-LSLV0220-H100;INV-LSLV0750-iS7 | E.OC | Over-current trip immediately at run command | Motor cable insulation breakdown (phase-to-phase short) | Disconnect motor cable, megger test cable and motor at 1,000 V | Replace damaged motor cable section | P2 | Y | N |  |  | 30
FLT-003 | DRIVE | INV-LSLV0075-S100;INV-LSLV0220-H100;INV-LSLV0750-iS7 | E.OC | Over-current trip even with motor disconnected | Output IGBT module damaged | Diode test on output terminals U/V/W shows short circuit | Replace power module under RMA | P2 | N | Y | IGBT power module |  | 120
FLT-004 | DRIVE | INV-LSLV0750-iS7 | E.OC | Over-current trip at restart after momentary power loss | Firmware defect in speed search at restart | Trip log shows E.OC within 50 ms after power restoration; reproducible with speed search enabled | Update firmware to 4.05 or later | P2 | N | N |  | 4.05 | 12
FLT-005 | DRIVE | INV-LSLV0075-S100;INV-LSLV0220-H100;INV-LSLV0750-iS7 | E.OV | Over-voltage trip during deceleration | Regenerative energy from load; deceleration time too short | Trip log shows DC link voltage > 820 V during DEC | Increase deceleration time or install braking resistor | P2 | N | N |  |  | 8
FLT-006 | DRIVE | INV-LSLV0075-S100;INV-LSLV0220-H100;INV-LSLV0750-iS7 | E.OV | Over-voltage trip at standstill | Supply voltage above tolerance (> 528 V) | Measure line voltage at drive input terminals | Adjust transformer tap or install input reactor | P3 | N | N |  |  | 48
FLT-007 | DRIVE | INV-LSLV0075-S100;INV-LSLV0220-H100;INV-LSLV0750-iS7 | E.LV | Low-voltage trip during operation | Loose input power terminal causing voltage drop | Measure input voltage under load; inspect terminal torque and discoloration | Retighten input terminals to specified torque | P2 | N | N |  |  | 8
FLT-008 | DRIVE | INV-LSLV0075-S100;INV-LSLV0220-H100;INV-LSLV0750-iS7 | E.LV | Low-voltage trip on one phase loss | Input fuse blown on one phase | Measure phase-to-phase input voltages | Replace input fuse and check upstream protection | P2 | N | N |  |  | 6
FLT-009 | DRIVE | INV-LSLV0075-S100;INV-LSLV0220-H100;INV-LSLV0750-iS7 | E.OL | Motor stops with overload trip | Motor rated current parameter set lower than motor nameplate | Compare motor rated current parameter with motor nameplate; check overload trip log | Correct motor rated current parameter and overload level | P3 | N | N |  |  | 4
FLT-010 | DRIVE | INV-LSLV0075-S100;INV-LSLV0220-H100;INV-LSLV0750-iS7 | E.OL | Overload trip after several minutes of operation | Mechanical jam / bearing failure in driven load | Load current trend rising over time; manual rotation check of load | Repair mechanical load; resume operation | P2 | N | N |  |  | 24
FLT-011 | DRIVE | INV-LSLV0075-S100;INV-LSLV0220-H100;INV-LSLV0750-iS7 | E.OH | Inverter overheat trip | Cooling fan failure | Check fan rotation and fan run-hour monitor | Replace cooling fan | P3 | N | N | Cooling fan |  | 24
FLT-012 | DRIVE | INV-LSLV0075-S100;INV-LSLV0220-H100;INV-LSLV0750-iS7 | E.OH | Overheat trip in summer afternoons | Panel ventilation insufficient; ambient > 50 °C | Measure panel internal temperature; check heat sink temperature monitor | Improve panel ventilation or apply derating | P3 | N | N |  |  | 72
FLT-013 | DRIVE | INV-LSLV0075-S100;INV-LSLV0220-H100;INV-LSLV0750-iS7 | E.GF | Ground fault trip | Motor winding insulation degradation | Megger test motor winding to ground (< 1 MΩ) | Repair or replace motor | P2 | Y | N |  |  | 48
FLT-014 | DRIVE | INV-LSLV0075-S100;INV-LSLV0220-H100;INV-LSLV0750-iS7 | E.PO | Output phase open trip | Loose motor terminal or contactor between drive and motor opened during run | Inspect motor wiring; check sequence of output contactor | Fix wiring and correct output contactor sequence | P3 | N | N |  |  | 8
FLT-015 | DRIVE | INV-LSLV0075-S100;INV-LSLV0220-H100;INV-LSLV0750-iS7 | E.CO | Communication error trip from PLC/BMS network | RS-485 termination missing or baud rate mismatch | Check communication parameters and termination resistor at both ends | Set matching baud rate and enable termination | P3 | N | N |  |  | 6
FLT-016 | DRIVE | INV-LSLV0075-S100 | E.CO | Intermittent communication error with fast polling | Firmware defect: Modbus response timeout below 20 ms polling | Reproduce with polling interval < 20 ms; firmware version 3.00 | Update firmware to 3.05 or later | P3 | N | N |  | 3.05 | 12
FLT-017 | DRIVE | INV-LSLV0220-H100 | E.CO | BACnet communication drops on large network | Firmware defect: MS/TP token loss with > 32 nodes | Network analyzer shows token loss; firmware older than 2.31 | Update firmware to 2.31 or later | P3 | N | N |  | 2.31 | 12
FLT-018 | DRIVE | INV-LSLV0075-S100 | E.EP | Parameter write error after keypad copy | Keypad parameter file from incompatible firmware version | Compare keypad source firmware with drive firmware | Update firmware to 3.10 and initialize parameters | P3 | N | N |  | 3.10 | 8
FLT-019 | DRIVE | INV-LSLV0075-S100;INV-LSLV0220-H100;INV-LSLV0750-iS7 |  | Motor does not run on remote command | Command source parameter set to keypad instead of terminal | Check run command source and frequency reference source parameters | Set command source to terminal/fieldbus | P4 | N | N |  |  | 2
FLT-020 | PLC | PLC-XGB-XBM-DR16S;PLC-XGI-CPUU | P.01 | CPU stops with watchdog error | Scan time exceeds watchdog due to program loop | Check max scan time in CPU status; review FOR/JMP loops | Fix program loop or increase watchdog setting | P2 | N | N |  |  | 8
FLT-021 | PLC | PLC-XGB-XBM-DR16S;PLC-XGI-CPUU | P.01 | Random watchdog error in noisy environment | Electrical noise due to improper grounding | Check FG grounding and cable shielding; correlate with contactor switching | Separate grounding and add surge suppressors | P2 | Y | N |  |  | 48
FLT-022 | PLC | PLC-XGB-XBM-DR16S;PLC-XGI-CPUU | P.02 | I/O configuration mismatch after module replacement | Replacement module type differs from I/O parameter | Compare I/O parameter with installed module list | Update I/O parameter and download | P3 | N | N |  |  | 4
FLT-023 | PLC | PLC-XGB-XBM-DR16S;PLC-XGI-CPUU | P.03 | Battery low warning | Backup battery end of life | Check battery voltage in CPU status | Replace backup battery (keep power on during replacement) | P4 | N | N | Backup battery |  | 4
FLT-024 | PLC | PLC-XGB-XBM-DR16S | P.04 | Program checksum error after power cycle | Firmware defect on repeated power cycling within 1 s | Event log shows power off/on within 1 s; firmware 3.00 | Re-download program and update firmware to 3.10 | P2 | N | N |  | 3.10 | 8
FLT-025 | PLC | PLC-XGB-XBM-DR16S;PLC-XGI-CPUU | P.04 | Program lost repeatedly | Flash memory failure in CPU | Checksum error recurs after re-download | Replace CPU under RMA | P2 | N | Y | CPU module |  | 120
FLT-026 | PLC | PLC-XGB-XBM-DR16S;PLC-XGI-CPUU | P.05 | Ethernet communication timeout | IP address conflict on plant network | ARP scan shows duplicate IP | Assign unique IP address | P3 | N | N |  |  | 4
FLT-027 | PLC | PLC-XGI-CPUU | P.05 | Ethernet timeout during broadcast storm | Firmware defect under broadcast storm > 2,000 frames/s | Packet capture shows broadcast storm; firmware older than 4.40 | Update firmware to 4.40 and configure switch storm control | P2 | N | N |  | 4.40 | 24
FLT-028 | PLC | PLC-XGB-XBM-DR16S;PLC-XGI-CPUU | P.06 | Base power fault, CPU does not start | Power supply module output degraded | Measure 5 V DC output of power module | Replace power supply module | P2 | N | Y | Power supply module |  | 72
FLT-029 | PLC | PLC-XGB-XBM-DR16S;PLC-XGI-CPUU |  | Relay output stuck ON | Relay contact welded by inrush of capacitive/lamp load | Output stays ON with CPU in STOP; check load type | Replace output module and add interposing relay | P3 | N | Y | Relay output module |  | 72
FLT-030 | HMI | HMI-XGT-eXP60;HMI-XGT-iXP90 | H.02 | PLC communication timeout on HMI | Driver protocol or station number mismatch | Compare HMI connection settings with PLC port settings | Correct protocol and station number | P3 | N | N |  |  | 4
FLT-031 | HMI | HMI-XGT-iXP90 | H.02 | Timeout when both Ethernet ports used | Firmware defect with two ports on same subnet | Firmware older than 2.05; ports on same subnet | Update OS to 2.05 or use separate subnets | P3 | N | N |  | 2.05 | 8
FLT-032 | HMI | HMI-XGT-eXP60 | H.03 | Project download fails | Editor version newer than HMI OS | Compare editor version with OS version | Update HMI OS to 1.62 or later | P3 | N | N |  | 1.62 | 4
FLT-033 | HMI | HMI-XGT-eXP60;HMI-XGT-iXP90 | H.01 | Touch position misaligned | Touch calibration drift | Run touch test in system menu | Recalibrate touch panel | P4 | N | N |  |  | 2
FLT-034 | HMI | HMI-XGT-eXP60;HMI-XGT-iXP90 | H.01 | Touch not responding in one area | Touch panel physically damaged | Visual inspection; touch test dead zone | Replace touch panel under RMA | P3 | N | Y | Touch panel |  | 96
FLT-035 | HMI | HMI-XGT-eXP60;HMI-XGT-iXP90 | H.04 | Screen very dark | Backlight end of life | Check operating hours (> 50,000 h) | Replace backlight / unit under RMA | P3 | N | Y | Backlight unit |  | 96
FLT-036 | HMI | HMI-XGT-eXP60;HMI-XGT-iXP90 | H.05 | Logging stops, memory full warning | Logging storage set to internal memory without rotation | Check logging configuration | Enable ring buffer or log to USB | P4 | N | N |  |  | 2
FLT-037 | HMI | HMI-XGT-eXP60 |  | Screen freezes after weeks of operation | Firmware defect after ~30 days uptime | Freeze reproducible after ~30 days; OS older than 1.58 | Update OS to 1.58 or later | P3 | N | N |  | 1.58 | 8
FLT-038 | LV_BREAKER | MCCB-ABS-103c;MCCB-ABS-403c |  | Breaker trips at motor start | Motor inrush exceeds magnetic trip setting | Measure starting current; compare with magnetic setting | Select breaker with higher magnetic setting or adjust | P3 | N | N |  |  | 8
FLT-039 | LV_BREAKER | MCCB-ABS-103c;MCCB-ABS-403c;ACB-AS-2000;ELCB-EBN-203c |  | Terminal overheating / discoloration | Loose connection or undersized cable | Thermographic inspection; check tightening torque | Retighten to specified torque; replace damaged terminal | P2 | Y | N |  |  | 24
FLT-040 | LV_BREAKER | MCCB-ABS-103c;MCCB-ABS-403c;ELCB-EBN-203c |  | Breaker cannot be reset after trip | Handle not moved to reset position before ON | Check handle position (trip / reset) | Push handle fully to OFF/RESET then ON | P4 | N | N |  |  | 1
FLT-041 | LV_BREAKER | MCCB-ABS-103c;MCCB-ABS-403c;ELCB-EBN-203c |  | Breaker does not close, mechanism damaged | Internal mechanism failure | Handle does not latch after reset | Replace breaker under warranty | P2 | N | Y |  |  | 72
FLT-042 | LV_BREAKER | ELCB-EBN-203c |  | Unwanted earth leakage trip | Cumulative leakage current from VFD EMC filters | Measure leakage current with clamp meter | Change sensitivity setting to 100/300 mA or separate circuits | P3 | N | N |  |  | 24
FLT-043 | LV_BREAKER | ELCB-EBN-203c |  | Test button does not trip ELCB | Residual current sensing circuit failure | Press test button at rated voltage; no trip | Replace ELCB immediately (safety) | P1 | N | Y |  |  | 48
FLT-044 | LV_BREAKER | ACB-AS-2000 | T.LT | ACB long-time trip | Sustained overload above long-time setting | Read trip unit event log current | Reduce load or adjust long-time setting per coordination study | P2 | N | N |  |  | 8
FLT-045 | LV_BREAKER | ACB-AS-2000 | T.GF | ACB ground fault trip | Insulation fault in downstream feeder | Insulation test of downstream feeders | Repair insulation fault before re-closing | P1 | Y | N |  |  | 24
FLT-046 | LV_BREAKER | ACB-AS-2000 | T.SF | ACB trip unit self-diagnosis alarm | Firmware defect after control power dip | Alarm after control voltage dip below 85 V; firmware older than 1.4 | Update trip unit firmware to 1.4 | P3 | N | N |  | 1.4 | 8
FLT-047 | LV_BREAKER | ACB-AS-2000 |  | ACB motor does not charge spring | Control voltage mismatch or motor fuse blown | Measure control voltage at motor terminals | Supply correct control voltage; replace fuse | P2 | N | N |  |  | 8
FLT-048 | MV_EQUIP | VCB-25kV-1250 |  | VCB spring not charging | Charging motor failure | Check control supply and motor current | Replace charging motor | P2 | Y | N | Charging motor |  | 48
FLT-049 | MV_EQUIP | VCB-25kV-1250 |  | VCB fails to close electrically | Closing coil burnt | Measure closing coil resistance | Replace closing coil | P2 | Y | N | Closing coil |  | 24
FLT-050 | MV_EQUIP | VCB-25kV-1250 |  | VCB contact wear indicator at limit | Vacuum interrupter end of electrical life | Check contact wear indicator; vacuum integrity test | Replace vacuum interrupter | P3 | Y | N | Vacuum interrupter |  | 72
FLT-051 | MV_EQUIP | SWGR-MV-12kV |  | Partial discharge alarm in switchgear | Condensation due to anti-condensation heater off | PD measurement and humidity check | Restore heater operation and clean insulators | P2 | Y | N |  |  | 48
FLT-052 | MV_EQUIP | SWGR-MV-12kV |  | Partial discharge at cable compartment | Cable termination workmanship defect | PD localisation; inspect cable termination | Re-terminate cable | P2 | Y | N |  |  | 72
FLT-053 | MV_EQUIP | SWGR-MV-12kV |  | Cable compartment door cannot be opened | Earthing switch not closed (interlock) | Check earthing switch position indicator | Follow operation sequence: open VCB, rack out, close earthing switch | P4 | N | N |  |  | 2
FLT-054 | MV_EQUIP | SWGR-MV-12kV |  | Busbar joint overheating | Insufficient joint torque | Thermographic inspection under load | Retorque busbar joints in outage | P2 | Y | N |  |  | 48
FLT-055 | MV_EQUIP | VCB-25kV-1250;SWGR-MV-12kV |  | Protection relay trip without fault | CT polarity reversed / wrong relay setting | Secondary injection test; check CT polarity | Correct CT wiring and relay settings | P2 | Y | N |  |  | 24
FLT-056 | CONTROL | CONT-MC-32a |  | Contactor chattering | Control voltage drops below pick-up level | Measure coil voltage during pick-up | Fix control supply capacity / cable length | P3 | N | N |  |  | 8
FLT-057 | CONTROL | CONT-MC-32a |  | Contactor coil burnt | Coil voltage different from supply voltage | Compare coil nameplate with supply | Replace coil with correct voltage | P3 | N | N | Coil |  | 24
FLT-058 | CONTROL | CONT-MC-32a |  | Main contacts welded | Short circuit without proper SCPD coordination | Review coordination type (Type 1/2) with upstream breaker | Replace contactor; apply Type 2 coordination | P2 | N | Y |  |  | 48
FLT-059 | CONTROL | RELAY-GMR-22 |  | Overload relay nuisance trip | Setting lower than motor full load current | Compare setting dial with motor FLC | Adjust setting to motor FLC | P3 | N | N |  |  | 2
FLT-060 | CONTROL | RELAY-GMR-22 |  | Overload relay does not trip on overload | Mechanism failure | Trip test with test button | Replace relay under warranty | P2 | N | Y |  |  | 48
FLT-061 | CONTROL | RELAY-GMR-22 |  | Overload relay trips on phase loss | Upstream fuse blown on one phase | Measure three phase currents | Replace fuse; check motor | P3 | N | N |  |  | 4
FLT-062 | TRANSFORMER | TRF-DRY-630 | A.TH1 | Winding temperature alarm (140 °C) | Cooling fans not operating under high load | Check fan operation and load current | Repair fan control; reduce load | P2 | N | N |  |  | 24
FLT-063 | TRANSFORMER | TRF-DRY-630;TRF-OIL-1000 |  | Abnormal humming noise | Loose core clamping or harmonic load | Sound level and harmonic measurement | Retighten clamping; apply harmonic filter | P3 | Y | N |  |  | 72
FLT-064 | TRANSFORMER | TRF-DRY-630 |  | Low insulation resistance before energisation | Moisture absorption during storage | IR / PI test of windings | Dry out with heaters and retest | P2 | Y | N |  |  | 72
FLT-065 | TRANSFORMER | TRF-OIL-1000 | A.BH1 | Buchholz alarm | Air trapped after oil filling | Gas sample test (air vs fault gas), DGA | Bleed air from Buchholz relay; monitor | P2 | Y | N |  |  | 24
FLT-066 | TRANSFORMER | TRF-OIL-1000 | A.BH2 | Buchholz trip | Internal winding fault | DGA shows acetylene; winding resistance test | Factory repair under warranty claim | P1 | Y | Y |  |  | 240
FLT-067 | TRANSFORMER | TRF-OIL-1000 |  | Oil leakage at gasket | Gasket damage during transport | Visual inspection of flanges | Replace gasket and top up oil | P3 | Y | N | Gasket set |  | 48
FLT-068 | TRANSFORMER | TRF-DRY-630;TRF-OIL-1000 |  | Secondary voltage too high | Off-circuit tap at wrong position | Measure secondary voltage and check tap | Change tap position in de-energised state | P3 | N | N |  |  | 8
FLT-069 | METER | METER-LP3500-3P4W;METER-LPB-DIN |  | Negative active power reading | CT polarity reversed | Check phase angle in meter diagnostics | Rewire CT or set CT reverse parameter | P4 | N | N |  |  | 4
FLT-070 | METER | METER-LP3500-3P4W;METER-LPB-DIN | R.01 | No Modbus response | Address / baud / parity mismatch | Compare master and meter comm settings | Align communication settings | P4 | N | N |  |  | 2
FLT-071 | METER | METER-LP3500-3P4W | R.01 | No response at 38400 even parity | Firmware defect at 38400 / even parity | Firmware older than 1.80 with 38400 E | Update firmware to 1.80 | P4 | N | N |  | 1.80 | 4
FLT-072 | METER | METER-LP3500-3P4W |  | Energy register reset after power loss | Firmware defect during flash write | Firmware older than 1.72 | Update firmware to 1.72 or later | P3 | N | N |  | 1.72 | 4
FLT-073 | METER | METER-LPB-DIN |  | Pulse output not counted by PLC | Open-collector output polarity reversed | Check wiring polarity | Correct polarity and pull-up | P4 | N | N |  |  | 2
FLT-074 | ESS | ESS-PCS-100kW | G.01 | Grid over-voltage trip | Wrong country grid profile selected | Check parameter G-01 grid profile | Select correct grid profile per utility requirement | P2 | N | N |  |  | 8
FLT-075 | ESS | ESS-PCS-100kW | G.02 | Frequency trip during generator operation | Firmware defect in ROCOF measurement | Trip during genset; firmware older than 2.70 | Update PCS firmware to 2.70 | P2 | N | N |  | 2.70 | 24
FLT-076 | ESS | ESS-PCS-100kW | G.04 | IGBT over-temperature | Air filter clogged | Inspect filters and fans | Clean/replace filters | P3 | N | N | Air filter |  | 24
FLT-077 | ESS | ESS-PCS-100kW;ESS-BMS-V3 | G.05 | DC insulation fault | Moisture in battery rack DC cabling | Insulation resistance test per rack | Dry and repair cabling | P1 | Y | N |  |  | 48
FLT-078 | ESS | ESS-PCS-100kW;ESS-BMS-V3 | G.06 | BMS communication loss on PCS | Firmware compatibility: BMS 3.4 heartbeat vs PCS < 2.62 | Check firmware versions of PCS and BMS | Update PCS firmware to 2.62 or later | P2 | N | N |  | 2.62 | 24
FLT-079 | ESS | ESS-PCS-100kW;ESS-BMS-V3 | G.06 | Intermittent CAN errors | CAN termination missing | Measure CAN bus resistance (expect 60 Ω) | Install 120 Ω termination | P3 | N | N |  |  | 8
FLT-080 | ESS | ESS-BMS-V3 | B.01 | Cell over-voltage alarm | Defective battery module cell | Cell voltage trend shows single cell drift | Replace battery module under RMA | P2 | Y | Y | Battery module |  | 120
FLT-081 | ESS | ESS-BMS-V3 | B.03 | Cell over-temperature | Container HVAC failure | Check HVAC alarm and room temperature | Stop operation; repair HVAC | P1 | Y | N |  |  | 24
FLT-082 | ESS | ESS-BMS-V3 | B.04 | Cell imbalance alarm | Insufficient balancing after long partial cycling | Max-min cell voltage difference > 50 mV | Perform full charge balancing maintenance | P3 | N | N |  |  | 48
FLT-083 | ESS | ESS-BMS-V3 | B.06 | Main contactor welded alarm | Pre-charge circuit failure | Pre-charge resistor measurement | Replace contactor and pre-charge resistor | P1 | Y | Y | DC contactor |  | 72
FLT-084 | ESS | ESS-BMS-V3 |  | SOC jumps after long rest | Firmware defect in SOC estimation | SOC trend shows jump; firmware older than 3.50 | Update BMS firmware to 3.50 and perform calibration | P3 | N | N |  | 3.50 | 24
FLT-085 | PV | PV-INV-SOLAR-25 | S.01 | Insulation fault at sunrise | Firmware defect at humidity > 95% | Fault only at sunrise; firmware older than 1.82 | Update firmware to 1.82 | P3 | N | N |  | 1.82 | 8
FLT-086 | PV | PV-INV-SOLAR-25 | S.01 | Insulation fault after rain | Water ingress in PV connector | IR test per string | Replace damaged connectors | P3 | Y | N |  |  | 48
FLT-087 | PV | PV-INV-SOLAR-25 | S.02 | Grid lost alarm | AC breaker tripped / grid outage | Measure AC voltage at inverter terminals | Restore AC supply; check breaker rating | P2 | N | N |  |  | 4
FLT-088 | PV | PV-INV-SOLAR-25 | S.03 | PV over-voltage alarm in winter | String too long for low temperature Voc | Recalculate Voc at minimum temperature | Reduce modules per string | P2 | N | N |  |  | 48
FLT-089 | PV | PV-INV-SOLAR-25 | S.04 | Power derating at noon | Installed in direct sunlight with poor airflow | Check heat sink temperature log | Relocate or add shading | P3 | N | N |  |  | 72
FLT-090 | PV | PV-INV-SOLAR-25 | S.05 | Residual current trip | Damaged DC cable insulation | Locate fault by string isolation | Repair cable | P2 | Y | N |  |  | 48
FLT-091 | PV | PV-INV-SOLAR-25 |  | Yield lower than expected | One string disconnected | Compare string currents | Reconnect string; check fuse | P3 | N | N |  |  | 8
FLT-092 | UPS | UPS-LSU-10K | U.01 | Short backup time | Battery end of life (> 3 years) | Run battery test; check battery age | Replace battery set | P3 | N | N | Battery set |  | 48
FLT-093 | UPS | UPS-LSU-10K | U.02 | UPS on bypass due to overload | Connected load exceeds rating | Read load % log | Redistribute load | P2 | N | N |  |  | 4
FLT-094 | UPS | UPS-LSU-10K | U.03 | Inverter fault, load on bypass | Inverter board failure | Event log U.03; self-test fails | Repair inverter board under RMA | P2 | N | Y | Inverter board |  | 120
FLT-095 | UPS | UPS-LSU-10K | U.05 | Over-temperature alarm | Fan failure | Check fan operation | Replace fan | P3 | N | N | Fan |  | 24
FLT-096 | UPS | UPS-LSU-10K |  | SNMP card not detected | Firmware defect after hot-swap | Firmware older than 2.30 | Update UPS firmware to 2.30 | P4 | N | N |  | 2.30 | 8
FLT-097 | UPS | UPS-LSU-10K |  | Frequent transfer to battery on generator | Generator frequency outside default window | Frequency log during genset operation | Enable generator mode (firmware 2.20 or later) | P3 | N | N |  | 2.20 | 8

## customers
customer_id | company_masked | country | tier | segment | account_since | contact_count
CUST-0001 | COMPANY_9869_0001 | IT | STANDARD | SYSTEM_INTEGRATOR | 2017-07-01 | 6
CUST-0002 | COMPANY_9166_0002 | IN | STANDARD | END_USER | 2017-05-01 | 4
CUST-0003 | COMPANY_5371_0003 | AU | STANDARD | DISTRIBUTOR | 2012-11-01 | 4
CUST-0004 | COMPANY_9393_0004 | JP | GOLD | DISTRIBUTOR | 2022-02-01 | 1
CUST-0005 | COMPANY_3101_0005 | JP | STANDARD | SYSTEM_INTEGRATOR | 2017-02-01 | 6
CUST-0006 | COMPANY_8439_0006 | GB | STANDARD | EPC | 2018-05-01 | 3
CUST-0007 | COMPANY_7415_0007 | MX | STANDARD | PANEL_BUILDER | 2018-03-01 | 4
CUST-0008 | COMPANY_4719_0008 | JP | PLATINUM | DISTRIBUTOR | 2019-06-01 | 1
CUST-0009 | COMPANY_7585_0009 | VN | STANDARD | EPC | 2012-06-01 | 5
CUST-0010 | COMPANY_5373_0010 | PL | GOLD | EPC | 2017-09-01 | 6
CUST-0011 | COMPANY_4028_0011 | ID | STANDARD | DISTRIBUTOR | 2022-07-01 | 4
CUST-0012 | COMPANY_3212_0012 | DE | GOLD | EPC | 2012-12-01 | 5
CUST-0013 | COMPANY_2350_0013 | GB | GOLD | EPC | 2023-08-01 | 2
CUST-0014 | COMPANY_8657_0014 | AE | GOLD | PANEL_BUILDER | 2016-01-01 | 4
CUST-0015 | COMPANY_3869_0015 | BR | GOLD | DISTRIBUTOR | 2024-07-01 | 4
CUST-0016 | COMPANY_8911_0016 | VN | STANDARD | DISTRIBUTOR | 2018-09-01 | 3
CUST-0017 | COMPANY_3772_0017 | AE | STANDARD | EPC | 2020-08-01 | 4
CUST-0018 | COMPANY_4548_0018 | US | STANDARD | PANEL_BUILDER | 2022-02-01 | 6
CUST-0019 | COMPANY_2892_0019 | ES | STANDARD | END_USER | 2025-07-01 | 1
CUST-0020 | COMPANY_1185_0020 | AU | STANDARD | UTILITY | 2024-08-01 | 4
CUST-0021 | COMPANY_5580_0021 | FR | GOLD | PANEL_BUILDER | 2025-11-01 | 2
CUST-0022 | COMPANY_5908_0022 | SA | STANDARD | EPC | 2022-07-01 | 6
CUST-0023 | COMPANY_7202_0023 | AU | STANDARD | SYSTEM_INTEGRATOR | 2019-11-01 | 1
CUST-0024 | COMPANY_6457_0024 | DE | STANDARD | END_USER | 2025-11-01 | 2
CUST-0025 | COMPANY_8971_0025 | TH | STANDARD | PANEL_BUILDER | 2021-03-01 | 3
CUST-0026 | COMPANY_5289_0026 | ES | STANDARD | EPC | 2016-07-01 | 4
CUST-0027 | COMPANY_2397_0027 | ES | STANDARD | PANEL_BUILDER | 2024-05-01 | 1
CUST-0028 | COMPANY_5036_0028 | GB | STANDARD | PANEL_BUILDER | 2017-08-01 | 3
CUST-0029 | COMPANY_7979_0029 | AU | GOLD | END_USER | 2021-06-01 | 3
CUST-0030 | COMPANY_1085_0030 | VN | STANDARD | UTILITY | 2019-05-01 | 4
CUST-0031 | COMPANY_6711_0031 | ID | STANDARD | END_USER | 2012-06-01 | 6
CUST-0032 | COMPANY_8511_0032 | AE | STANDARD | PANEL_BUILDER | 2023-07-01 | 4
CUST-0033 | COMPANY_1263_0033 | IN | STANDARD | EPC | 2021-01-01 | 3
CUST-0034 | COMPANY_6558_0034 | MX | STANDARD | UTILITY | 2015-07-01 | 6
CUST-0035 | COMPANY_6708_0035 | US | STANDARD | END_USER | 2017-02-01 | 1
CUST-0036 | COMPANY_9821_0036 | TR | STANDARD | EPC | 2018-08-01 | 6
CUST-0037 | COMPANY_5376_0037 | US | GOLD | END_USER | 2019-12-01 | 3
CUST-0038 | COMPANY_1444_0038 | DE | STANDARD | PANEL_BUILDER | 2025-06-01 | 3
CUST-0039 | COMPANY_1852_0039 | MX | GOLD | EPC | 2024-09-01 | 3
CUST-0040 | COMPANY_2189_0040 | GB | GOLD | END_USER | 2024-08-01 | 1
CUST-0041 | COMPANY_5343_0041 | SA | GOLD | SYSTEM_INTEGRATOR | 2019-06-01 | 6
CUST-0042 | COMPANY_8505_0042 | TH | PLATINUM | END_USER | 2020-06-01 | 4
CUST-0043 | COMPANY_4296_0043 | AU | PLATINUM | PANEL_BUILDER | 2013-01-01 | 5
CUST-0044 | COMPANY_7279_0044 | RU | STANDARD | DISTRIBUTOR | 2012-07-01 | 6
CUST-0045 | COMPANY_7412_0045 | IN | STANDARD | EPC | 2016-01-01 | 5
CUST-0046 | COMPANY_8206_0046 | AE | STANDARD | PANEL_BUILDER | 2023-10-01 | 4
CUST-0047 | COMPANY_9422_0047 | GB | STANDARD | DISTRIBUTOR | 2013-02-01 | 3
CUST-0048 | COMPANY_1424_0048 | RU | STANDARD | DISTRIBUTOR | 2023-02-01 | 4
CUST-0049 | COMPANY_1517_0049 | US | STANDARD | SYSTEM_INTEGRATOR | 2019-04-01 | 5
CUST-0050 | COMPANY_6100_0050 | MX | PLATINUM | UTILITY | 2015-07-01 | 3
CUST-0051 | COMPANY_5277_0051 | TR | STANDARD | END_USER | 2013-08-01 | 5
CUST-0052 | COMPANY_2190_0052 | GB | STANDARD | END_USER | 2018-11-01 | 3
CUST-0053 | COMPANY_1066_0053 | AE | STANDARD | DISTRIBUTOR | 2021-12-01 | 6
CUST-0054 | COMPANY_3590_0054 | FR | STANDARD | EPC | 2017-10-01 | 2
CUST-0055 | COMPANY_1563_0055 | ID | STANDARD | PANEL_BUILDER | 2021-02-01 | 6
CUST-0056 | COMPANY_1826_0056 | FR | GOLD | PANEL_BUILDER | 2020-08-01 | 5
CUST-0057 | COMPANY_5984_0057 | VN | STANDARD | EPC | 2023-01-01 | 6
CUST-0058 | COMPANY_3729_0058 | MX | STANDARD | EPC | 2017-04-01 | 1
CUST-0059 | COMPANY_8687_0059 | IN | STANDARD | DISTRIBUTOR | 2022-12-01 | 5
CUST-0060 | COMPANY_9925_0060 | AE | PLATINUM | DISTRIBUTOR | 2015-04-01 | 1
CUST-0061 | COMPANY_7069_0061 | RU | STANDARD | END_USER | 2014-04-01 | 3
CUST-0062 | COMPANY_8302_0062 | IT | STANDARD | EPC | 2024-04-01 | 3
CUST-0063 | COMPANY_9694_0063 | ID | STANDARD | DISTRIBUTOR | 2013-03-01 | 5
CUST-0064 | COMPANY_4148_0064 | JP | STANDARD | END_USER | 2017-06-01 | 6
CUST-0065 | COMPANY_2471_0065 | BR | GOLD | PANEL_BUILDER | 2019-01-01 | 4
CUST-0066 | COMPANY_7822_0066 | PL | STANDARD | EPC | 2022-06-01 | 4
CUST-0067 | COMPANY_5775_0067 | RU | STANDARD | SYSTEM_INTEGRATOR | 2021-05-01 | 1
CUST-0068 | COMPANY_6818_0068 | DE | STANDARD | DISTRIBUTOR | 2024-05-01 | 6
CUST-0069 | COMPANY_4767_0069 | TR | STANDARD | EPC | 2023-09-01 | 5
CUST-0070 | COMPANY_5481_0070 | MX | GOLD | DISTRIBUTOR | 2015-03-01 | 1
CUST-0071 | COMPANY_5233_0071 | GB | GOLD | PANEL_BUILDER | 2025-05-01 | 5
CUST-0072 | COMPANY_6602_0072 | ID | GOLD | UTILITY | 2025-09-01 | 2
CUST-0073 | COMPANY_4965_0073 | VN | STANDARD | UTILITY | 2025-12-01 | 5
CUST-0074 | COMPANY_1468_0074 | DE | STANDARD | SYSTEM_INTEGRATOR | 2015-07-01 | 4
CUST-0075 | COMPANY_1758_0075 | RU | STANDARD | EPC | 2012-11-01 | 2
CUST-0076 | COMPANY_1713_0076 | BR | GOLD | EPC | 2012-01-01 | 1
CUST-0077 | COMPANY_3063_0077 | VN | GOLD | END_USER | 2022-11-01 | 6
CUST-0078 | COMPANY_3689_0078 | TH | STANDARD | DISTRIBUTOR | 2016-12-01 | 6
CUST-0079 | COMPANY_9836_0079 | SA | GOLD | PANEL_BUILDER | 2012-11-01 | 2
CUST-0080 | COMPANY_6055_0080 | ES | GOLD | PANEL_BUILDER | 2018-08-01 | 4
CUST-0081 | COMPANY_9685_0081 | US | PLATINUM | DISTRIBUTOR | 2020-09-01 | 6
CUST-0082 | COMPANY_2749_0082 | CN | GOLD | PANEL_BUILDER | 2023-09-01 | 2
CUST-0083 | COMPANY_5326_0083 | SA | STANDARD | DISTRIBUTOR | 2021-08-01 | 2
CUST-0084 | COMPANY_1493_0084 | IN | STANDARD | PANEL_BUILDER | 2020-04-01 | 1
CUST-0085 | COMPANY_1701_0085 | US | STANDARD | EPC | 2018-05-01 | 3
CUST-0086 | COMPANY_2582_0086 | US | GOLD | DISTRIBUTOR | 2023-04-01 | 1
CUST-0087 | COMPANY_6841_0087 | BR | GOLD | EPC | 2021-06-01 | 6
CUST-0088 | COMPANY_4928_0088 | RU | PLATINUM | EPC | 2015-09-01 | 1
CUST-0089 | COMPANY_6818_0089 | GB | STANDARD | PANEL_BUILDER | 2023-05-01 | 2
CUST-0090 | COMPANY_5368_0090 | VN | STANDARD | SYSTEM_INTEGRATOR | 2019-10-01 | 6
CUST-0091 | COMPANY_4749_0091 | VN | STANDARD | PANEL_BUILDER | 2012-01-01 | 2
CUST-0092 | COMPANY_4877_0092 | VN | STANDARD | EPC | 2014-08-01 | 2
CUST-0093 | COMPANY_1614_0093 | ES | GOLD | UTILITY | 2013-05-01 | 3
CUST-0094 | COMPANY_5865_0094 | JP | STANDARD | EPC | 2014-11-01 | 6
CUST-0095 | COMPANY_3357_0095 | US | STANDARD | SYSTEM_INTEGRATOR | 2022-01-01 | 3
CUST-0096 | COMPANY_2326_0096 | IT | STANDARD | DISTRIBUTOR | 2016-12-01 | 1
CUST-0097 | COMPANY_7533_0097 | CN | STANDARD | DISTRIBUTOR | 2016-07-01 | 4
CUST-0098 | COMPANY_6094_0098 | IT | STANDARD | DISTRIBUTOR | 2017-01-01 | 5
CUST-0099 | COMPANY_2494_0099 | FR | STANDARD | END_USER | 2013-08-01 | 4
CUST-0100 | COMPANY_1011_0100 | IT | GOLD | EPC | 2016-11-01 | 6
CUST-0101 | COMPANY_7252_0101 | DE | STANDARD | PANEL_BUILDER | 2019-01-01 | 5
CUST-0102 | COMPANY_2817_0102 | DE | GOLD | SYSTEM_INTEGRATOR | 2023-04-01 | 5
CUST-0103 | COMPANY_9145_0103 | ID | GOLD | END_USER | 2020-08-01 | 3
CUST-0104 | COMPANY_3147_0104 | FR | STANDARD | DISTRIBUTOR | 2019-10-01 | 5
CUST-0105 | COMPANY_9757_0105 | AE | STANDARD | PANEL_BUILDER | 2022-11-01 | 5
CUST-0106 | COMPANY_3740_0106 | AE | PLATINUM | DISTRIBUTOR | 2012-05-01 | 1
CUST-0107 | COMPANY_6827_0107 | IN | GOLD | DISTRIBUTOR | 2014-02-01 | 2
CUST-0108 | COMPANY_3371_0108 | JP | STANDARD | DISTRIBUTOR | 2022-09-01 | 5
CUST-0109 | COMPANY_3039_0109 | AU | GOLD | PANEL_BUILDER | 2013-04-01 | 5
CUST-0110 | COMPANY_3755_0110 | TH | STANDARD | PANEL_BUILDER | 2013-08-01 | 4
CUST-0111 | COMPANY_6837_0111 | PL | STANDARD | EPC | 2018-01-01 | 4
CUST-0112 | COMPANY_3809_0112 | CN | STANDARD | DISTRIBUTOR | 2014-09-01 | 1
CUST-0113 | COMPANY_2444_0113 | TH | STANDARD | END_USER | 2022-08-01 | 1
CUST-0114 | COMPANY_3979_0114 | DE | STANDARD | EPC | 2016-11-01 | 2
CUST-0115 | COMPANY_6076_0115 | MX | STANDARD | EPC | 2013-03-01 | 4
CUST-0116 | COMPANY_8187_0116 | DE | STANDARD | UTILITY | 2018-09-01 | 2
CUST-0117 | COMPANY_2549_0117 | RU | STANDARD | PANEL_BUILDER | 2024-07-01 | 6
CUST-0118 | COMPANY_7823_0118 | TH | STANDARD | END_USER | 2015-01-01 | 3
CUST-0119 | COMPANY_6176_0119 | GB | GOLD | DISTRIBUTOR | 2012-10-01 | 2
CUST-0120 | COMPANY_5338_0120 | US | STANDARD | EPC | 2017-12-01 | 4
CUST-0121 | COMPANY_7834_0121 | AE | STANDARD | EPC | 2022-07-01 | 6
CUST-0122 | COMPANY_8882_0122 | AU | STANDARD | PANEL_BUILDER | 2022-10-01 | 3
CUST-0123 | COMPANY_2049_0123 | ID | STANDARD | END_USER | 2014-01-01 | 3
CUST-0124 | COMPANY_3776_0124 | SA | GOLD | EPC | 2024-07-01 | 4
CUST-0125 | COMPANY_3370_0125 | ES | STANDARD | EPC | 2016-10-01 | 4
CUST-0126 | COMPANY_5647_0126 | ID | GOLD | SYSTEM_INTEGRATOR | 2013-06-01 | 3
CUST-0127 | COMPANY_5941_0127 | FR | STANDARD | PANEL_BUILDER | 2016-10-01 | 5
CUST-0128 | COMPANY_5099_0128 | US | STANDARD | DISTRIBUTOR | 2022-03-01 | 3
CUST-0129 | COMPANY_9431_0129 | IN | GOLD | END_USER | 2018-06-01 | 6
CUST-0130 | COMPANY_3859_0130 | ID | PLATINUM | SYSTEM_INTEGRATOR | 2020-06-01 | 2
CUST-0131 | COMPANY_3593_0131 | GB | STANDARD | END_USER | 2014-06-01 | 4
CUST-0132 | COMPANY_9437_0132 | GB | GOLD | EPC | 2019-06-01 | 4
CUST-0133 | COMPANY_8374_0133 | ID | GOLD | EPC | 2014-01-01 | 5
CUST-0134 | COMPANY_1876_0134 | DE | STANDARD | EPC | 2016-12-01 | 4
CUST-0135 | COMPANY_1289_0135 | IN | PLATINUM | END_USER | 2012-02-01 | 3
CUST-0136 | COMPANY_3210_0136 | AE | GOLD | END_USER | 2012-12-01 | 3
CUST-0137 | COMPANY_8254_0137 | SA | STANDARD | END_USER | 2020-05-01 | 5
CUST-0138 | COMPANY_7514_0138 | IT | STANDARD | DISTRIBUTOR | 2016-04-01 | 5
CUST-0139 | COMPANY_6195_0139 | ID | STANDARD | EPC | 2018-06-01 | 2
CUST-0140 | COMPANY_5887_0140 | GB | GOLD | EPC | 2022-04-01 | 4
CUST-0141 | COMPANY_7080_0141 | TH | STANDARD | EPC | 2019-10-01 | 2
CUST-0142 | COMPANY_2043_0142 | AE | GOLD | END_USER | 2023-08-01 | 4
CUST-0143 | COMPANY_7228_0143 | ES | STANDARD | SYSTEM_INTEGRATOR | 2014-09-01 | 5
CUST-0144 | COMPANY_6039_0144 | GB | GOLD | SYSTEM_INTEGRATOR | 2016-04-01 | 3
CUST-0145 | COMPANY_2494_0145 | AU | STANDARD | END_USER | 2025-03-01 | 5
CUST-0146 | COMPANY_4880_0146 | CN | STANDARD | SYSTEM_INTEGRATOR | 2012-08-01 | 1
CUST-0147 | COMPANY_4257_0147 | ES | PLATINUM | EPC | 2012-09-01 | 3
CUST-0148 | COMPANY_9602_0148 | CN | GOLD | EPC | 2022-08-01 | 5
CUST-0149 | COMPANY_8095_0149 | TR | GOLD | DISTRIBUTOR | 2022-03-01 | 1
CUST-0150 | COMPANY_6609_0150 | AE | PLATINUM | EPC | 2012-01-01 | 6
CUST-0151 | COMPANY_4986_0151 | VN | GOLD | DISTRIBUTOR | 2023-06-01 | 6
CUST-0152 | COMPANY_1480_0152 | GB | STANDARD | END_USER | 2016-07-01 | 2
CUST-0153 | COMPANY_7168_0153 | US | STANDARD | PANEL_BUILDER | 2022-08-01 | 4
CUST-0154 | COMPANY_5493_0154 | IT | PLATINUM | PANEL_BUILDER | 2025-08-01 | 5
CUST-0155 | COMPANY_5974_0155 | IN | STANDARD | SYSTEM_INTEGRATOR | 2018-02-01 | 2
CUST-0156 | COMPANY_3157_0156 | IN | GOLD | END_USER | 2023-02-01 | 1
CUST-0157 | COMPANY_8233_0157 | US | STANDARD | PANEL_BUILDER | 2014-03-01 | 6
CUST-0158 | COMPANY_8889_0158 | TR | STANDARD | EPC | 2013-07-01 | 1
CUST-0159 | COMPANY_8736_0159 | IN | STANDARD | END_USER | 2023-05-01 | 1
CUST-0160 | COMPANY_3039_0160 | IN | PLATINUM | UTILITY | 2016-09-01 | 1
CUST-0161 | COMPANY_7296_0161 | RU | STANDARD | END_USER | 2023-08-01 | 6
CUST-0162 | COMPANY_5381_0162 | US | GOLD | SYSTEM_INTEGRATOR | 2016-10-01 | 6
CUST-0163 | COMPANY_1004_0163 | SA | PLATINUM | END_USER | 2017-07-01 | 6
CUST-0164 | COMPANY_6855_0164 | ID | STANDARD | EPC | 2025-08-01 | 1
CUST-0165 | COMPANY_8607_0165 | TH | STANDARD | END_USER | 2025-03-01 | 5
CUST-0166 | COMPANY_3917_0166 | GB | STANDARD | DISTRIBUTOR | 2020-07-01 | 6
CUST-0167 | COMPANY_5355_0167 | GB | STANDARD | DISTRIBUTOR | 2021-04-01 | 1
CUST-0168 | COMPANY_8790_0168 | PL | GOLD | PANEL_BUILDER | 2021-02-01 | 5
CUST-0169 | COMPANY_4409_0169 | MX | STANDARD | DISTRIBUTOR | 2018-11-01 | 2
CUST-0170 | COMPANY_2521_0170 | RU | GOLD | PANEL_BUILDER | 2017-02-01 | 4
CUST-0171 | COMPANY_6762_0171 | US | STANDARD | UTILITY | 2019-09-01 | 6
CUST-0172 | COMPANY_2611_0172 | DE | GOLD | END_USER | 2023-09-01 | 5
CUST-0173 | COMPANY_8490_0173 | RU | STANDARD | DISTRIBUTOR | 2023-03-01 | 3
CUST-0174 | COMPANY_2786_0174 | FR | STANDARD | DISTRIBUTOR | 2023-01-01 | 1
CUST-0175 | COMPANY_9782_0175 | US | GOLD | END_USER | 2025-12-01 | 3
CUST-0176 | COMPANY_7520_0176 | ID | STANDARD | END_USER | 2025-09-01 | 1
CUST-0177 | COMPANY_9178_0177 | IN | STANDARD | END_USER | 2021-08-01 | 2
CUST-0178 | COMPANY_4090_0178 | TR | GOLD | EPC | 2025-03-01 | 1
CUST-0179 | COMPANY_3681_0179 | JP | STANDARD | PANEL_BUILDER | 2017-05-01 | 4
CUST-0180 | COMPANY_4642_0180 | FR | STANDARD | EPC | 2019-04-01 | 4
CUST-0181 | COMPANY_3309_0181 | FR | STANDARD | END_USER | 2018-12-01 | 3
CUST-0182 | COMPANY_6736_0182 | ID | STANDARD | EPC | 2019-09-01 | 3
CUST-0183 | COMPANY_4975_0183 | FR | GOLD | DISTRIBUTOR | 2019-11-01 | 2
CUST-0184 | COMPANY_8312_0184 | BR | STANDARD | DISTRIBUTOR | 2012-01-01 | 4
CUST-0185 | COMPANY_5486_0185 | AE | GOLD | EPC | 2016-08-01 | 1
CUST-0186 | COMPANY_1798_0186 | AU | GOLD | END_USER | 2023-08-01 | 5
CUST-0187 | COMPANY_1833_0187 | FR | PLATINUM | SYSTEM_INTEGRATOR | 2015-08-01 | 2
CUST-0188 | COMPANY_6840_0188 | AE | STANDARD | UTILITY | 2023-07-01 | 5
CUST-0189 | COMPANY_2490_0189 | ID | STANDARD | DISTRIBUTOR | 2025-06-01 | 6
CUST-0190 | COMPANY_4078_0190 | VN | STANDARD | PANEL_BUILDER | 2016-10-01 | 6
CUST-0191 | COMPANY_2034_0191 | AE | STANDARD | DISTRIBUTOR | 2022-04-01 | 5
CUST-0192 | COMPANY_3624_0192 | TR | GOLD | END_USER | 2014-06-01 | 6
CUST-0193 | COMPANY_8253_0193 | ID | STANDARD | END_USER | 2016-01-01 | 3
CUST-0194 | COMPANY_4131_0194 | TH | STANDARD | EPC | 2017-09-01 | 3
CUST-0195 | COMPANY_5916_0195 | RU | STANDARD | DISTRIBUTOR | 2018-08-01 | 6
CUST-0196 | COMPANY_7815_0196 | FR | STANDARD | PANEL_BUILDER | 2015-03-01 | 6
CUST-0197 | COMPANY_6952_0197 | ES | STANDARD | SYSTEM_INTEGRATOR | 2022-12-01 | 6
CUST-0198 | COMPANY_6349_0198 | MX | PLATINUM | EPC | 2019-05-01 | 2
CUST-0199 | COMPANY_1909_0199 | BR | STANDARD | PANEL_BUILDER | 2013-06-01 | 6
CUST-0200 | COMPANY_3221_0200 | MX | STANDARD | END_USER | 2014-11-01 | 3
CUST-0201 | COMPANY_9240_0201 | TR | GOLD | END_USER | 2018-09-01 | 6
CUST-0202 | COMPANY_9520_0202 | VN | STANDARD | PANEL_BUILDER | 2012-03-01 | 1
CUST-0203 | COMPANY_1429_0203 | TR | PLATINUM | PANEL_BUILDER | 2012-02-01 | 6
CUST-0204 | COMPANY_3048_0204 | RU | GOLD | END_USER | 2017-05-01 | 1
CUST-0205 | COMPANY_4078_0205 | DE | GOLD | PANEL_BUILDER | 2019-05-01 | 1
CUST-0206 | COMPANY_5644_0206 | US | GOLD | PANEL_BUILDER | 2017-12-01 | 4
CUST-0207 | COMPANY_6037_0207 | MX | GOLD | END_USER | 2022-10-01 | 2
CUST-0208 | COMPANY_9248_0208 | CN | STANDARD | DISTRIBUTOR | 2022-02-01 | 3
CUST-0209 | COMPANY_8472_0209 | TH | PLATINUM | EPC | 2022-12-01 | 2
CUST-0210 | COMPANY_9447_0210 | SA | STANDARD | EPC | 2017-02-01 | 2
CUST-0211 | COMPANY_3021_0211 | GB | GOLD | END_USER | 2022-01-01 | 2
CUST-0212 | COMPANY_3568_0212 | TH | STANDARD | END_USER | 2015-11-01 | 5
CUST-0213 | COMPANY_4553_0213 | AU | STANDARD | SYSTEM_INTEGRATOR | 2013-08-01 | 1
CUST-0214 | COMPANY_9841_0214 | AE | STANDARD | SYSTEM_INTEGRATOR | 2025-06-01 | 5
CUST-0215 | COMPANY_1253_0215 | BR | PLATINUM | PANEL_BUILDER | 2014-11-01 | 5
CUST-0216 | COMPANY_9403_0216 | ID | STANDARD | UTILITY | 2012-06-01 | 1
CUST-0217 | COMPANY_4625_0217 | AE | STANDARD | PANEL_BUILDER | 2013-03-01 | 2
CUST-0218 | COMPANY_2479_0218 | AU | GOLD | EPC | 2025-07-01 | 6
CUST-0219 | COMPANY_2784_0219 | JP | STANDARD | DISTRIBUTOR | 2020-05-01 | 6
CUST-0220 | COMPANY_6288_0220 | TH | GOLD | PANEL_BUILDER | 2012-01-01 | 6
CUST-0221 | COMPANY_4502_0221 | FR | STANDARD | DISTRIBUTOR | 2022-04-01 | 3
CUST-0222 | COMPANY_9910_0222 | VN | GOLD | PANEL_BUILDER | 2022-06-01 | 1
CUST-0223 | COMPANY_9844_0223 | US | STANDARD | END_USER | 2014-12-01 | 6
CUST-0224 | COMPANY_7719_0224 | IN | STANDARD | EPC | 2019-12-01 | 1
CUST-0225 | COMPANY_7174_0225 | VN | PLATINUM | PANEL_BUILDER | 2019-06-01 | 2
CUST-0226 | COMPANY_3059_0226 | FR | STANDARD | DISTRIBUTOR | 2014-09-01 | 6
CUST-0227 | COMPANY_4607_0227 | CN | PLATINUM | PANEL_BUILDER | 2024-04-01 | 6
CUST-0228 | COMPANY_3456_0228 | IT | GOLD | EPC | 2021-09-01 | 4
CUST-0229 | COMPANY_7953_0229 | IT | STANDARD | SYSTEM_INTEGRATOR | 2018-07-01 | 2
CUST-0230 | COMPANY_4683_0230 | CN | STANDARD | EPC | 2013-02-01 | 5
CUST-0231 | COMPANY_9238_0231 | CN | STANDARD | SYSTEM_INTEGRATOR | 2024-09-01 | 1
CUST-0232 | COMPANY_8157_0232 | TH | GOLD | PANEL_BUILDER | 2022-01-01 | 1
CUST-0233 | COMPANY_3918_0233 | RU | STANDARD | DISTRIBUTOR | 2015-06-01 | 6
CUST-0234 | COMPANY_3984_0234 | SA | STANDARD | DISTRIBUTOR | 2012-05-01 | 6
CUST-0235 | COMPANY_5668_0235 | ID | STANDARD | PANEL_BUILDER | 2022-10-01 | 6
CUST-0236 | COMPANY_2608_0236 | ES | STANDARD | DISTRIBUTOR | 2021-11-01 | 2
CUST-0237 | COMPANY_5409_0237 | FR | STANDARD | END_USER | 2018-05-01 | 3
CUST-0238 | COMPANY_8218_0238 | MX | STANDARD | END_USER | 2014-02-01 | 1
CUST-0239 | COMPANY_7852_0239 | IT | STANDARD | END_USER | 2021-04-01 | 5
CUST-0240 | COMPANY_7418_0240 | AE | STANDARD | PANEL_BUILDER | 2019-07-01 | 3
CUST-0241 | COMPANY_4496_0241 | CN | STANDARD | EPC | 2025-01-01 | 2
CUST-0242 | COMPANY_4954_0242 | GB | STANDARD | PANEL_BUILDER | 2023-09-01 | 1
CUST-0243 | COMPANY_6198_0243 | MX | GOLD | END_USER | 2013-03-01 | 4
CUST-0244 | COMPANY_2648_0244 | RU | STANDARD | EPC | 2020-06-01 | 5
CUST-0245 | COMPANY_7954_0245 | SA | STANDARD | EPC | 2018-03-01 | 1
CUST-0246 | COMPANY_6851_0246 | FR | STANDARD | EPC | 2023-08-01 | 4
CUST-0247 | COMPANY_6060_0247 | SA | PLATINUM | END_USER | 2013-06-01 | 5
CUST-0248 | COMPANY_1574_0248 | GB | STANDARD | END_USER | 2021-06-01 | 3
CUST-0249 | COMPANY_3236_0249 | ID | GOLD | EPC | 2023-10-01 | 3
CUST-0250 | COMPANY_7533_0250 | TH | STANDARD | DISTRIBUTOR | 2012-05-01 | 1
CUST-0251 | COMPANY_6601_0251 | DE | STANDARD | END_USER | 2014-12-01 | 4
CUST-0252 | COMPANY_1185_0252 | VN | GOLD | END_USER | 2019-05-01 | 6
CUST-0253 | COMPANY_3828_0253 | IN | STANDARD | EPC | 2013-03-01 | 5
CUST-0254 | COMPANY_1435_0254 | IT | STANDARD | EPC | 2019-03-01 | 1
CUST-0255 | COMPANY_7056_0255 | BR | STANDARD | EPC | 2020-12-01 | 4
CUST-0256 | COMPANY_8291_0256 | AU | GOLD | DISTRIBUTOR | 2014-03-01 | 4
CUST-0257 | COMPANY_2618_0257 | GB | GOLD | DISTRIBUTOR | 2022-10-01 | 2
CUST-0258 | COMPANY_3498_0258 | TH | STANDARD | EPC | 2017-03-01 | 4
CUST-0259 | COMPANY_7692_0259 | TH | STANDARD | DISTRIBUTOR | 2021-06-01 | 4
CUST-0260 | COMPANY_7948_0260 | TR | STANDARD | END_USER | 2024-09-01 | 1
CUST-0261 | COMPANY_5764_0261 | BR | GOLD | PANEL_BUILDER | 2023-04-01 | 3
CUST-0262 | COMPANY_5427_0262 | AE | GOLD | END_USER | 2025-08-01 | 3
CUST-0263 | COMPANY_1211_0263 | DE | STANDARD | PANEL_BUILDER | 2015-10-01 | 3
CUST-0264 | COMPANY_8048_0264 | IN | STANDARD | PANEL_BUILDER | 2024-08-01 | 3
CUST-0265 | COMPANY_4165_0265 | FR | PLATINUM | END_USER | 2019-10-01 | 5
CUST-0266 | COMPANY_2063_0266 | RU | STANDARD | DISTRIBUTOR | 2023-07-01 | 3
CUST-0267 | COMPANY_1961_0267 | FR | GOLD | DISTRIBUTOR | 2016-03-01 | 2
CUST-0268 | COMPANY_1142_0268 | GB | STANDARD | DISTRIBUTOR | 2012-03-01 | 6
CUST-0269 | COMPANY_4740_0269 | IN | STANDARD | EPC | 2018-06-01 | 1
CUST-0270 | COMPANY_6164_0270 | CN | STANDARD | END_USER | 2023-04-01 | 6
CUST-0271 | COMPANY_3604_0271 | AU | STANDARD | EPC | 2025-09-01 | 3
CUST-0272 | COMPANY_8909_0272 | FR | STANDARD | DISTRIBUTOR | 2023-05-01 | 4
CUST-0273 | COMPANY_9150_0273 | CN | PLATINUM | EPC | 2016-12-01 | 2
CUST-0274 | COMPANY_4349_0274 | AE | GOLD | PANEL_BUILDER | 2015-03-01 | 4
CUST-0275 | COMPANY_8325_0275 | US | STANDARD | END_USER | 2020-08-01 | 4
CUST-0276 | COMPANY_9669_0276 | DE | STANDARD | UTILITY | 2012-10-01 | 5
CUST-0277 | COMPANY_1532_0277 | FR | STANDARD | DISTRIBUTOR | 2017-12-01 | 1
CUST-0278 | COMPANY_5729_0278 | TH | PLATINUM | END_USER | 2016-01-01 | 2
CUST-0279 | COMPANY_4063_0279 | CN | PLATINUM | PANEL_BUILDER | 2013-05-01 | 2
CUST-0280 | COMPANY_5478_0280 | DE | STANDARD | END_USER | 2019-05-01 | 5
CUST-0281 | COMPANY_4361_0281 | FR | STANDARD | EPC | 2023-01-01 | 1
CUST-0282 | COMPANY_5914_0282 | US | PLATINUM | PANEL_BUILDER | 2014-07-01 | 4
CUST-0283 | COMPANY_5254_0283 | BR | STANDARD | SYSTEM_INTEGRATOR | 2019-11-01 | 5
CUST-0284 | COMPANY_1720_0284 | DE | PLATINUM | END_USER | 2019-01-01 | 6
CUST-0285 | COMPANY_3161_0285 | DE | GOLD | END_USER | 2022-05-01 | 4
CUST-0286 | COMPANY_2682_0286 | CN | STANDARD | UTILITY | 2020-09-01 | 1
CUST-0287 | COMPANY_1318_0287 | BR | STANDARD | EPC | 2023-04-01 | 2
CUST-0288 | COMPANY_3147_0288 | VN | STANDARD | END_USER | 2022-04-01 | 2
CUST-0289 | COMPANY_7612_0289 | VN | GOLD | PANEL_BUILDER | 2017-01-01 | 6
CUST-0290 | COMPANY_4808_0290 | RU | STANDARD | EPC | 2015-09-01 | 2
CUST-0291 | COMPANY_3767_0291 | IN | STANDARD | DISTRIBUTOR | 2012-11-01 | 6
CUST-0292 | COMPANY_3274_0292 | TH | STANDARD | SYSTEM_INTEGRATOR | 2015-06-01 | 6
CUST-0293 | COMPANY_5556_0293 | SA | PLATINUM | EPC | 2022-05-01 | 5
CUST-0294 | COMPANY_5023_0294 | JP | PLATINUM | UTILITY | 2017-08-01 | 4
CUST-0295 | COMPANY_2700_0295 | CN | GOLD | END_USER | 2025-06-01 | 5
CUST-0296 | COMPANY_4910_0296 | AU | GOLD | EPC | 2015-02-01 | 2
CUST-0297 | COMPANY_6137_0297 | PL | GOLD | DISTRIBUTOR | 2022-06-01 | 6
CUST-0298 | COMPANY_5630_0298 | SA | STANDARD | EPC | 2016-11-01 | 2
CUST-0299 | COMPANY_3998_0299 | AE | GOLD | END_USER | 2021-05-01 | 2
CUST-0300 | COMPANY_7026_0300 | JP | STANDARD | SYSTEM_INTEGRATOR | 2021-04-01 | 5
CUST-0301 | COMPANY_9044_0301 | ES | GOLD | DISTRIBUTOR | 2016-01-01 | 3
CUST-0302 | COMPANY_6192_0302 | IN | STANDARD | END_USER | 2016-10-01 | 1
CUST-0303 | COMPANY_1650_0303 | AU | STANDARD | DISTRIBUTOR | 2020-04-01 | 5
CUST-0304 | COMPANY_6265_0304 | US | GOLD | END_USER | 2012-02-01 | 5
CUST-0305 | COMPANY_3222_0305 | BR | STANDARD | DISTRIBUTOR | 2013-09-01 | 2
CUST-0306 | COMPANY_6282_0306 | ID | STANDARD | EPC | 2020-03-01 | 1
CUST-0307 | COMPANY_4254_0307 | JP | STANDARD | UTILITY | 2023-10-01 | 2
CUST-0308 | COMPANY_9063_0308 | ES | PLATINUM | EPC | 2023-05-01 | 5
CUST-0309 | COMPANY_2081_0309 | PL | STANDARD | END_USER | 2022-10-01 | 4
CUST-0310 | COMPANY_4984_0310 | AE | STANDARD | PANEL_BUILDER | 2020-03-01 | 5
CUST-0311 | COMPANY_7931_0311 | DE | STANDARD | END_USER | 2022-10-01 | 6
CUST-0312 | COMPANY_6831_0312 | FR | STANDARD | END_USER | 2025-04-01 | 5
CUST-0313 | COMPANY_6858_0313 | RU | GOLD | PANEL_BUILDER | 2017-10-01 | 2
CUST-0314 | COMPANY_3990_0314 | ES | GOLD | UTILITY | 2017-01-01 | 4
CUST-0315 | COMPANY_7813_0315 | VN | STANDARD | SYSTEM_INTEGRATOR | 2014-02-01 | 1
CUST-0316 | COMPANY_4970_0316 | IT | STANDARD | SYSTEM_INTEGRATOR | 2021-04-01 | 3
CUST-0317 | COMPANY_9177_0317 | ES | PLATINUM | EPC | 2022-04-01 | 4
CUST-0318 | COMPANY_2277_0318 | IT | STANDARD | DISTRIBUTOR | 2025-11-01 | 4
CUST-0319 | COMPANY_9233_0319 | TR | GOLD | DISTRIBUTOR | 2013-12-01 | 4
CUST-0320 | COMPANY_7488_0320 | JP | GOLD | UTILITY | 2014-11-01 | 5
CUST-0321 | COMPANY_4874_0321 | ES | STANDARD | SYSTEM_INTEGRATOR | 2016-09-01 | 1
CUST-0322 | COMPANY_7274_0322 | AE | STANDARD | END_USER | 2014-02-01 | 1
CUST-0323 | COMPANY_7435_0323 | ES | GOLD | PANEL_BUILDER | 2025-06-01 | 1
CUST-0324 | COMPANY_7443_0324 | PL | STANDARD | DISTRIBUTOR | 2014-06-01 | 3
CUST-0325 | COMPANY_2368_0325 | US | PLATINUM | EPC | 2023-12-01 | 2
CUST-0326 | COMPANY_5373_0326 | TH | GOLD | DISTRIBUTOR | 2013-06-01 | 1
CUST-0327 | COMPANY_5286_0327 | MX | GOLD | EPC | 2023-06-01 | 4
CUST-0328 | COMPANY_1082_0328 | TR | STANDARD | PANEL_BUILDER | 2016-10-01 | 2
CUST-0329 | COMPANY_8268_0329 | JP | STANDARD | DISTRIBUTOR | 2024-06-01 | 3
CUST-0330 | COMPANY_4020_0330 | RU | STANDARD | EPC | 2018-08-01 | 2
CUST-0331 | COMPANY_6288_0331 | RU | STANDARD | UTILITY | 2017-10-01 | 1
CUST-0332 | COMPANY_2036_0332 | ID | GOLD | DISTRIBUTOR | 2025-05-01 | 6
CUST-0333 | COMPANY_8056_0333 | GB | STANDARD | SYSTEM_INTEGRATOR | 2017-02-01 | 3
CUST-0334 | COMPANY_5942_0334 | GB | STANDARD | END_USER | 2019-08-01 | 1
CUST-0335 | COMPANY_4557_0335 | IN | GOLD | PANEL_BUILDER | 2021-01-01 | 2
CUST-0336 | COMPANY_5815_0336 | RU | STANDARD | EPC | 2019-04-01 | 4
CUST-0337 | COMPANY_3106_0337 | BR | STANDARD | PANEL_BUILDER | 2013-06-01 | 5
CUST-0338 | COMPANY_6134_0338 | PL | STANDARD | PANEL_BUILDER | 2024-01-01 | 3
CUST-0339 | COMPANY_6591_0339 | DE | STANDARD | DISTRIBUTOR | 2016-08-01 | 1
CUST-0340 | COMPANY_6378_0340 | GB | GOLD | END_USER | 2021-11-01 | 4
CUST-0341 | COMPANY_4051_0341 | IT | GOLD | SYSTEM_INTEGRATOR | 2021-02-01 | 6
CUST-0342 | COMPANY_2746_0342 | GB | GOLD | END_USER | 2017-02-01 | 4
CUST-0343 | COMPANY_8742_0343 | ES | GOLD | PANEL_BUILDER | 2023-02-01 | 2
CUST-0344 | COMPANY_3441_0344 | JP | PLATINUM | PANEL_BUILDER | 2021-11-01 | 5
CUST-0345 | COMPANY_7374_0345 | CN | STANDARD | END_USER | 2016-10-01 | 1
CUST-0346 | COMPANY_4385_0346 | BR | STANDARD | DISTRIBUTOR | 2016-05-01 | 1
CUST-0347 | COMPANY_5991_0347 | IT | STANDARD | EPC | 2015-05-01 | 2
CUST-0348 | COMPANY_1441_0348 | MX | GOLD | END_USER | 2013-08-01 | 1
CUST-0349 | COMPANY_3010_0349 | DE | STANDARD | PANEL_BUILDER | 2022-04-01 | 3
CUST-0350 | COMPANY_2801_0350 | TH | PLATINUM | EPC | 2014-07-01 | 2
CUST-0351 | COMPANY_7265_0351 | SA | STANDARD | UTILITY | 2024-07-01 | 1
CUST-0352 | COMPANY_2817_0352 | DE | GOLD | END_USER | 2014-05-01 | 2
CUST-0353 | COMPANY_1949_0353 | FR | STANDARD | DISTRIBUTOR | 2013-11-01 | 4
CUST-0354 | COMPANY_9914_0354 | GB | STANDARD | END_USER | 2019-11-01 | 6
CUST-0355 | COMPANY_8568_0355 | GB | STANDARD | PANEL_BUILDER | 2012-02-01 | 1
CUST-0356 | COMPANY_1953_0356 | ES | PLATINUM | DISTRIBUTOR | 2020-04-01 | 4
CUST-0357 | COMPANY_8173_0357 | US | STANDARD | DISTRIBUTOR | 2023-08-01 | 3
CUST-0358 | COMPANY_4974_0358 | ID | STANDARD | PANEL_BUILDER | 2015-05-01 | 3
CUST-0359 | COMPANY_4388_0359 | FR | GOLD | END_USER | 2014-03-01 | 2
CUST-0360 | COMPANY_4047_0360 | GB | STANDARD | DISTRIBUTOR | 2018-06-01 | 5
CUST-0361 | COMPANY_4698_0361 | JP | GOLD | EPC | 2018-05-01 | 5
CUST-0362 | COMPANY_5866_0362 | GB | STANDARD | EPC | 2024-06-01 | 1
CUST-0363 | COMPANY_4093_0363 | AE | PLATINUM | EPC | 2019-04-01 | 2
CUST-0364 | COMPANY_7875_0364 | AU | GOLD | EPC | 2025-09-01 | 6
CUST-0365 | COMPANY_7774_0365 | MX | PLATINUM | EPC | 2023-07-01 | 1
CUST-0366 | COMPANY_4042_0366 | ID | STANDARD | PANEL_BUILDER | 2013-08-01 | 6
CUST-0367 | COMPANY_8080_0367 | SA | STANDARD | EPC | 2022-06-01 | 3
CUST-0368 | COMPANY_7691_0368 | US | GOLD | EPC | 2012-01-01 | 1
CUST-0369 | COMPANY_6469_0369 | MX | STANDARD | EPC | 2022-09-01 | 3
CUST-0370 | COMPANY_8540_0370 | IN | STANDARD | EPC | 2018-03-01 | 6
CUST-0371 | COMPANY_2719_0371 | AE | STANDARD | EPC | 2020-01-01 | 1
CUST-0372 | COMPANY_6006_0372 | PL | PLATINUM | DISTRIBUTOR | 2020-04-01 | 6
CUST-0373 | COMPANY_7895_0373 | US | GOLD | PANEL_BUILDER | 2023-04-01 | 3
CUST-0374 | COMPANY_3540_0374 | TR | GOLD | DISTRIBUTOR | 2022-09-01 | 1
CUST-0375 | COMPANY_2286_0375 | SA | STANDARD | END_USER | 2014-04-01 | 4
CUST-0376 | COMPANY_6460_0376 | US | GOLD | PANEL_BUILDER | 2016-08-01 | 5
CUST-0377 | COMPANY_6522_0377 | US | GOLD | END_USER | 2020-11-01 | 4
CUST-0378 | COMPANY_8287_0378 | ES | GOLD | EPC | 2025-12-01 | 5
CUST-0379 | COMPANY_4375_0379 | MX | STANDARD | EPC | 2024-07-01 | 2
CUST-0380 | COMPANY_4878_0380 | IT | PLATINUM | END_USER | 2012-06-01 | 6
CUST-0381 | COMPANY_1878_0381 | GB | STANDARD | DISTRIBUTOR | 2012-07-01 | 5
CUST-0382 | COMPANY_6475_0382 | ID | STANDARD | END_USER | 2025-06-01 | 1
CUST-0383 | COMPANY_7499_0383 | GB | GOLD | SYSTEM_INTEGRATOR | 2017-06-01 | 5
CUST-0384 | COMPANY_4078_0384 | IN | STANDARD | EPC | 2021-12-01 | 1
CUST-0385 | COMPANY_3487_0385 | SA | PLATINUM | END_USER | 2015-11-01 | 3
CUST-0386 | COMPANY_1131_0386 | MX | STANDARD | PANEL_BUILDER | 2021-09-01 | 2
CUST-0387 | COMPANY_3216_0387 | GB | STANDARD | PANEL_BUILDER | 2014-10-01 | 1
CUST-0388 | COMPANY_8902_0388 | IN | STANDARD | END_USER | 2025-03-01 | 4
CUST-0389 | COMPANY_1726_0389 | VN | STANDARD | END_USER | 2020-07-01 | 1
CUST-0390 | COMPANY_3838_0390 | VN | STANDARD | UTILITY | 2021-02-01 | 2
CUST-0391 | COMPANY_6047_0391 | MX | GOLD | PANEL_BUILDER | 2014-01-01 | 6
CUST-0392 | COMPANY_2736_0392 | BR | STANDARD | EPC | 2021-01-01 | 2
CUST-0393 | COMPANY_9796_0393 | US | STANDARD | DISTRIBUTOR | 2019-02-01 | 6
CUST-0394 | COMPANY_5001_0394 | US | STANDARD | PANEL_BUILDER | 2019-01-01 | 3
CUST-0395 | COMPANY_4664_0395 | ES | STANDARD | DISTRIBUTOR | 2015-02-01 | 5
CUST-0396 | COMPANY_4987_0396 | TR | PLATINUM | DISTRIBUTOR | 2017-09-01 | 6
CUST-0397 | COMPANY_9290_0397 | CN | STANDARD | EPC | 2022-09-01 | 6
CUST-0398 | COMPANY_9158_0398 | ID | GOLD | EPC | 2020-10-01 | 4
CUST-0399 | COMPANY_9503_0399 | ID | STANDARD | SYSTEM_INTEGRATOR | 2017-06-01 | 2
CUST-0400 | COMPANY_8554_0400 | TR | GOLD | EPC | 2022-02-01 | 5
CUST-0401 | COMPANY_1475_0401 | FR | PLATINUM | DISTRIBUTOR | 2017-05-01 | 2
CUST-0402 | COMPANY_4463_0402 | AE | STANDARD | END_USER | 2024-05-01 | 6
CUST-0403 | COMPANY_9056_0403 | IT | STANDARD | END_USER | 2017-05-01 | 3
CUST-0404 | COMPANY_6437_0404 | ES | STANDARD | EPC | 2015-08-01 | 6
CUST-0405 | COMPANY_4042_0405 | PL | STANDARD | END_USER | 2024-09-01 | 5
CUST-0406 | COMPANY_4869_0406 | TH | STANDARD | END_USER | 2013-06-01 | 4
CUST-0407 | COMPANY_1391_0407 | AU | STANDARD | DISTRIBUTOR | 2018-05-01 | 2
CUST-0408 | COMPANY_2369_0408 | ID | STANDARD | DISTRIBUTOR | 2018-03-01 | 3
CUST-0409 | COMPANY_1759_0409 | AE | STANDARD | SYSTEM_INTEGRATOR | 2019-07-01 | 6
CUST-0410 | COMPANY_4344_0410 | RU | STANDARD | END_USER | 2019-04-01 | 4
CUST-0411 | COMPANY_1653_0411 | JP | STANDARD | DISTRIBUTOR | 2018-01-01 | 2
CUST-0412 | COMPANY_7860_0412 | TH | STANDARD | DISTRIBUTOR | 2021-12-01 | 6
CUST-0413 | COMPANY_1363_0413 | IT | STANDARD | SYSTEM_INTEGRATOR | 2020-12-01 | 6
CUST-0414 | COMPANY_9294_0414 | TH | STANDARD | EPC | 2013-11-01 | 1
CUST-0415 | COMPANY_3865_0415 | FR | STANDARD | DISTRIBUTOR | 2017-04-01 | 2
CUST-0416 | COMPANY_7957_0416 | IT | STANDARD | DISTRIBUTOR | 2023-08-01 | 2
CUST-0417 | COMPANY_9898_0417 | IT | STANDARD | DISTRIBUTOR | 2020-06-01 | 6
CUST-0418 | COMPANY_8413_0418 | CN | STANDARD | EPC | 2016-09-01 | 3
CUST-0419 | COMPANY_6129_0419 | MX | STANDARD | EPC | 2013-07-01 | 4
CUST-0420 | COMPANY_9295_0420 | FR | STANDARD | PANEL_BUILDER | 2021-09-01 | 5
CUST-0421 | COMPANY_9508_0421 | US | STANDARD | PANEL_BUILDER | 2024-12-01 | 1
CUST-0422 | COMPANY_8659_0422 | TR | STANDARD | EPC | 2021-09-01 | 1
CUST-0423 | COMPANY_4784_0423 | CN | STANDARD | END_USER | 2025-04-01 | 5
CUST-0424 | COMPANY_1027_0424 | BR | STANDARD | DISTRIBUTOR | 2015-06-01 | 5
CUST-0425 | COMPANY_3516_0425 | US | STANDARD | PANEL_BUILDER | 2015-02-01 | 1
CUST-0426 | COMPANY_3320_0426 | IN | STANDARD | EPC | 2025-02-01 | 3
CUST-0427 | COMPANY_9006_0427 | FR | GOLD | END_USER | 2022-01-01 | 5
CUST-0428 | COMPANY_1835_0428 | TH | STANDARD | SYSTEM_INTEGRATOR | 2017-02-01 | 6
CUST-0429 | COMPANY_2072_0429 | TR | GOLD | UTILITY | 2012-07-01 | 3
CUST-0430 | COMPANY_8740_0430 | PL | STANDARD | DISTRIBUTOR | 2020-11-01 | 4
CUST-0431 | COMPANY_7453_0431 | AE | GOLD | EPC | 2023-07-01 | 2
CUST-0432 | COMPANY_9314_0432 | GB | GOLD | PANEL_BUILDER | 2014-12-01 | 5
CUST-0433 | COMPANY_9541_0433 | VN | GOLD | SYSTEM_INTEGRATOR | 2022-12-01 | 2
CUST-0434 | COMPANY_5086_0434 | IN | STANDARD | END_USER | 2017-03-01 | 3
CUST-0435 | COMPANY_8002_0435 | TH | STANDARD | DISTRIBUTOR | 2024-08-01 | 4
CUST-0436 | COMPANY_2464_0436 | TH | GOLD | END_USER | 2020-08-01 | 3
CUST-0437 | COMPANY_9676_0437 | IT | PLATINUM | DISTRIBUTOR | 2021-04-01 | 5
CUST-0438 | COMPANY_4932_0438 | AE | GOLD | END_USER | 2013-06-01 | 5
CUST-0439 | COMPANY_6483_0439 | TR | STANDARD | EPC | 2024-07-01 | 5
CUST-0440 | COMPANY_5399_0440 | PL | STANDARD | DISTRIBUTOR | 2024-03-01 | 3
CUST-0441 | COMPANY_7130_0441 | ID | STANDARD | DISTRIBUTOR | 2017-01-01 | 4
CUST-0442 | COMPANY_9368_0442 | MX | STANDARD | END_USER | 2019-06-01 | 6
CUST-0443 | COMPANY_9041_0443 | CN | STANDARD | DISTRIBUTOR | 2023-09-01 | 3
CUST-0444 | COMPANY_7429_0444 | IN | STANDARD | UTILITY | 2025-11-01 | 2
CUST-0445 | COMPANY_5360_0445 | CN | STANDARD | PANEL_BUILDER | 2013-06-01 | 3
CUST-0446 | COMPANY_4262_0446 | MX | STANDARD | PANEL_BUILDER | 2022-12-01 | 1
CUST-0447 | COMPANY_9586_0447 | BR | GOLD | EPC | 2020-04-01 | 2
CUST-0448 | COMPANY_1466_0448 | ES | STANDARD | DISTRIBUTOR | 2023-03-01 | 2
CUST-0449 | COMPANY_4755_0449 | AU | STANDARD | EPC | 2024-03-01 | 1
CUST-0450 | COMPANY_3633_0450 | AU | STANDARD | EPC | 2015-04-01 | 6
CUST-0451 | COMPANY_8748_0451 | TH | GOLD | END_USER | 2021-12-01 | 3
CUST-0452 | COMPANY_2870_0452 | ID | STANDARD | DISTRIBUTOR | 2017-08-01 | 5
CUST-0453 | COMPANY_9435_0453 | MX | GOLD | EPC | 2019-04-01 | 1
CUST-0454 | COMPANY_7443_0454 | TR | STANDARD | DISTRIBUTOR | 2019-07-01 | 5
CUST-0455 | COMPANY_2383_0455 | US | STANDARD | DISTRIBUTOR | 2024-08-01 | 1
CUST-0456 | COMPANY_8729_0456 | AU | STANDARD | PANEL_BUILDER | 2019-06-01 | 6
CUST-0457 | COMPANY_8919_0457 | IN | GOLD | EPC | 2025-09-01 | 2
CUST-0458 | COMPANY_7407_0458 | RU | STANDARD | DISTRIBUTOR | 2016-06-01 | 4
CUST-0459 | COMPANY_7587_0459 | DE | STANDARD | SYSTEM_INTEGRATOR | 2020-12-01 | 1
CUST-0460 | COMPANY_2608_0460 | GB | STANDARD | EPC | 2015-05-01 | 3
CUST-0461 | COMPANY_7430_0461 | FR | STANDARD | DISTRIBUTOR | 2024-10-01 | 4
CUST-0462 | COMPANY_6741_0462 | AU | GOLD | DISTRIBUTOR | 2017-11-01 | 3
CUST-0463 | COMPANY_5321_0463 | PL | STANDARD | PANEL_BUILDER | 2016-02-01 | 3
CUST-0464 | COMPANY_3266_0464 | RU | STANDARD | EPC | 2016-03-01 | 1
CUST-0465 | COMPANY_3134_0465 | FR | STANDARD | END_USER | 2015-11-01 | 5
CUST-0466 | COMPANY_1244_0466 | JP | STANDARD | DISTRIBUTOR | 2016-12-01 | 3
CUST-0467 | COMPANY_3292_0467 | AU | STANDARD | END_USER | 2021-12-01 | 2
CUST-0468 | COMPANY_6199_0468 | TR | STANDARD | DISTRIBUTOR | 2024-06-01 | 5
CUST-0469 | COMPANY_4945_0469 | AE | STANDARD | DISTRIBUTOR | 2019-12-01 | 2
CUST-0470 | COMPANY_6049_0470 | FR | STANDARD | END_USER | 2025-01-01 | 2
CUST-0471 | COMPANY_7404_0471 | AE | STANDARD | END_USER | 2018-11-01 | 1
CUST-0472 | COMPANY_8764_0472 | MX | GOLD | EPC | 2023-08-01 | 4
CUST-0473 | COMPANY_6105_0473 | GB | STANDARD | PANEL_BUILDER | 2025-12-01 | 2
CUST-0474 | COMPANY_4211_0474 | TH | GOLD | SYSTEM_INTEGRATOR | 2015-12-01 | 1
CUST-0475 | COMPANY_3002_0475 | RU | STANDARD | PANEL_BUILDER | 2016-03-01 | 6
CUST-0476 | COMPANY_3326_0476 | SA | GOLD | DISTRIBUTOR | 2025-10-01 | 4
CUST-0477 | COMPANY_5043_0477 | SA | STANDARD | SYSTEM_INTEGRATOR | 2017-10-01 | 6
CUST-0478 | COMPANY_4287_0478 | GB | STANDARD | EPC | 2025-02-01 | 2
CUST-0479 | COMPANY_1316_0479 | US | STANDARD | PANEL_BUILDER | 2021-12-01 | 1
CUST-0480 | COMPANY_8005_0480 | IT | STANDARD | END_USER | 2021-06-01 | 1
CUST-0481 | COMPANY_3351_0481 | GB | STANDARD | DISTRIBUTOR | 2013-12-01 | 6
CUST-0482 | COMPANY_6118_0482 | US | STANDARD | PANEL_BUILDER | 2012-09-01 | 2
CUST-0483 | COMPANY_7989_0483 | ES | PLATINUM | SYSTEM_INTEGRATOR | 2015-02-01 | 4
CUST-0484 | COMPANY_4715_0484 | ES | GOLD | DISTRIBUTOR | 2022-10-01 | 6
CUST-0485 | COMPANY_6483_0485 | FR | STANDARD | EPC | 2021-12-01 | 1
CUST-0486 | COMPANY_6997_0486 | US | STANDARD | EPC | 2023-01-01 | 1
CUST-0487 | COMPANY_1067_0487 | SA | STANDARD | PANEL_BUILDER | 2023-07-01 | 4
CUST-0488 | COMPANY_7379_0488 | TH | STANDARD | PANEL_BUILDER | 2015-11-01 | 1
CUST-0489 | COMPANY_6236_0489 | VN | GOLD | END_USER | 2021-09-01 | 6
CUST-0490 | COMPANY_9330_0490 | TR | STANDARD | PANEL_BUILDER | 2019-07-01 | 6
CUST-0491 | COMPANY_7040_0491 | FR | GOLD | PANEL_BUILDER | 2015-09-01 | 4
CUST-0492 | COMPANY_1851_0492 | JP | STANDARD | PANEL_BUILDER | 2024-11-01 | 3
CUST-0493 | COMPANY_3515_0493 | MX | GOLD | EPC | 2017-12-01 | 5
CUST-0494 | COMPANY_3180_0494 | BR | STANDARD | PANEL_BUILDER | 2013-08-01 | 3
CUST-0495 | COMPANY_8493_0495 | TR | STANDARD | EPC | 2016-12-01 | 6
CUST-0496 | COMPANY_2862_0496 | IT | GOLD | PANEL_BUILDER | 2014-01-01 | 1
CUST-0497 | COMPANY_3642_0497 | TR | STANDARD | END_USER | 2018-09-01 | 4
CUST-0498 | COMPANY_1227_0498 | GB | GOLD | DISTRIBUTOR | 2025-08-01 | 6
CUST-0499 | COMPANY_2150_0499 | AU | GOLD | UTILITY | 2023-09-01 | 2
CUST-0500 | COMPANY_1789_0500 | RU | GOLD | DISTRIBUTOR | 2021-03-01 | 2
CUST-0501 | COMPANY_8122_0501 | CN | GOLD | EPC | 2013-10-01 | 1
CUST-0502 | COMPANY_1269_0502 | ID | STANDARD | PANEL_BUILDER | 2012-02-01 | 5
CUST-0503 | COMPANY_3853_0503 | RU | GOLD | UTILITY | 2014-08-01 | 5
CUST-0504 | COMPANY_8180_0504 | VN | STANDARD | DISTRIBUTOR | 2020-12-01 | 6
CUST-0505 | COMPANY_1841_0505 | GB | STANDARD | END_USER | 2018-12-01 | 5
CUST-0506 | COMPANY_8007_0506 | CN | STANDARD | END_USER | 2023-05-01 | 1
CUST-0507 | COMPANY_5772_0507 | BR | STANDARD | PANEL_BUILDER | 2024-12-01 | 5
CUST-0508 | COMPANY_1302_0508 | MX | PLATINUM | EPC | 2014-03-01 | 3
CUST-0509 | COMPANY_3987_0509 | RU | PLATINUM | DISTRIBUTOR | 2024-04-01 | 2
CUST-0510 | COMPANY_3792_0510 | BR | STANDARD | PANEL_BUILDER | 2013-09-01 | 2
CUST-0511 | COMPANY_4519_0511 | GB | GOLD | DISTRIBUTOR | 2022-02-01 | 4
CUST-0512 | COMPANY_2482_0512 | CN | STANDARD | DISTRIBUTOR | 2013-09-01 | 3
CUST-0513 | COMPANY_8560_0513 | ES | GOLD | PANEL_BUILDER | 2025-03-01 | 3
CUST-0514 | COMPANY_9834_0514 | TR | STANDARD | DISTRIBUTOR | 2014-09-01 | 5
CUST-0515 | COMPANY_4979_0515 | GB | STANDARD | EPC | 2023-09-01 | 1
CUST-0516 | COMPANY_6289_0516 | DE | STANDARD | UTILITY | 2019-08-01 | 6
CUST-0517 | COMPANY_2190_0517 | SA | PLATINUM | DISTRIBUTOR | 2015-11-01 | 6
CUST-0518 | COMPANY_8007_0518 | BR | STANDARD | EPC | 2012-09-01 | 6
CUST-0519 | COMPANY_8499_0519 | US | STANDARD | END_USER | 2023-12-01 | 2
CUST-0520 | COMPANY_2392_0520 | FR | STANDARD | PANEL_BUILDER | 2015-02-01 | 2
CUST-0521 | COMPANY_8723_0521 | VN | GOLD | UTILITY | 2019-05-01 | 5
CUST-0522 | COMPANY_5229_0522 | IT | PLATINUM | EPC | 2023-12-01 | 2
CUST-0523 | COMPANY_7797_0523 | GB | GOLD | END_USER | 2019-03-01 | 2
CUST-0524 | COMPANY_1788_0524 | IN | GOLD | EPC | 2017-05-01 | 4
CUST-0525 | COMPANY_8184_0525 | PL | STANDARD | EPC | 2019-05-01 | 4
CUST-0526 | COMPANY_3545_0526 | US | GOLD | DISTRIBUTOR | 2025-01-01 | 5
CUST-0527 | COMPANY_6999_0527 | MX | STANDARD | SYSTEM_INTEGRATOR | 2012-10-01 | 4
CUST-0528 | COMPANY_4100_0528 | JP | STANDARD | EPC | 2021-01-01 | 2
CUST-0529 | COMPANY_4839_0529 | CN | STANDARD | DISTRIBUTOR | 2016-02-01 | 1
CUST-0530 | COMPANY_9450_0530 | MX | GOLD | PANEL_BUILDER | 2016-10-01 | 4
CUST-0531 | COMPANY_1615_0531 | FR | PLATINUM | DISTRIBUTOR | 2015-08-01 | 3
CUST-0532 | COMPANY_5494_0532 | JP | STANDARD | DISTRIBUTOR | 2024-12-01 | 1
CUST-0533 | COMPANY_7197_0533 | CN | GOLD | DISTRIBUTOR | 2019-08-01 | 5
CUST-0534 | COMPANY_9345_0534 | DE | STANDARD | END_USER | 2019-09-01 | 3
CUST-0535 | COMPANY_8915_0535 | TH | GOLD | EPC | 2023-08-01 | 2
CUST-0536 | COMPANY_4033_0536 | TR | STANDARD | END_USER | 2018-06-01 | 4
CUST-0537 | COMPANY_6184_0537 | AU | STANDARD | END_USER | 2013-12-01 | 1
CUST-0538 | COMPANY_2953_0538 | TR | STANDARD | PANEL_BUILDER | 2021-10-01 | 6
CUST-0539 | COMPANY_3608_0539 | GB | STANDARD | PANEL_BUILDER | 2016-03-01 | 1
CUST-0540 | COMPANY_4638_0540 | TR | STANDARD | END_USER | 2025-11-01 | 2
CUST-0541 | COMPANY_7762_0541 | IN | STANDARD | PANEL_BUILDER | 2015-10-01 | 1
CUST-0542 | COMPANY_1318_0542 | BR | STANDARD | DISTRIBUTOR | 2022-02-01 | 3
CUST-0543 | COMPANY_5218_0543 | PL | STANDARD | SYSTEM_INTEGRATOR | 2014-10-01 | 4
CUST-0544 | COMPANY_3879_0544 | MX | STANDARD | DISTRIBUTOR | 2017-12-01 | 1
CUST-0545 | COMPANY_9555_0545 | US | STANDARD | PANEL_BUILDER | 2015-03-01 | 4
CUST-0546 | COMPANY_9135_0546 | AE | STANDARD | EPC | 2014-11-01 | 6
CUST-0547 | COMPANY_3640_0547 | SA | GOLD | END_USER | 2024-12-01 | 1
CUST-0548 | COMPANY_8546_0548 | ID | STANDARD | EPC | 2022-07-01 | 6
CUST-0549 | COMPANY_3566_0549 | TR | STANDARD | DISTRIBUTOR | 2017-04-01 | 5
CUST-0550 | COMPANY_9889_0550 | TR | STANDARD | PANEL_BUILDER | 2025-12-01 | 2
CUST-0551 | COMPANY_7314_0551 | DE | STANDARD | EPC | 2017-10-01 | 3
CUST-0552 | COMPANY_7164_0552 | FR | GOLD | DISTRIBUTOR | 2021-11-01 | 2
CUST-0553 | COMPANY_5839_0553 | AU | STANDARD | SYSTEM_INTEGRATOR | 2023-05-01 | 1
CUST-0554 | COMPANY_3958_0554 | ES | STANDARD | UTILITY | 2025-01-01 | 5
CUST-0555 | COMPANY_9753_0555 | ES | STANDARD | EPC | 2022-11-01 | 1
CUST-0556 | COMPANY_7728_0556 | AU | GOLD | EPC | 2023-02-01 | 4
CUST-0557 | COMPANY_4616_0557 | US | STANDARD | SYSTEM_INTEGRATOR | 2015-06-01 | 6
CUST-0558 | COMPANY_9374_0558 | BR | STANDARD | PANEL_BUILDER | 2020-08-01 | 2
CUST-0559 | COMPANY_5137_0559 | SA | STANDARD | PANEL_BUILDER | 2018-03-01 | 3
CUST-0560 | COMPANY_9186_0560 | FR | STANDARD | PANEL_BUILDER | 2025-06-01 | 6
CUST-0561 | COMPANY_4131_0561 | IN | STANDARD | END_USER | 2023-04-01 | 4
CUST-0562 | COMPANY_7242_0562 | ES | STANDARD | UTILITY | 2018-04-01 | 3
CUST-0563 | COMPANY_2866_0563 | MX | STANDARD | END_USER | 2012-12-01 | 1
CUST-0564 | COMPANY_1629_0564 | SA | STANDARD | PANEL_BUILDER | 2015-11-01 | 4
CUST-0565 | COMPANY_4800_0565 | TR | STANDARD | PANEL_BUILDER | 2019-07-01 | 4
CUST-0566 | COMPANY_2377_0566 | ID | STANDARD | PANEL_BUILDER | 2015-07-01 | 1
CUST-0567 | COMPANY_7575_0567 | AU | STANDARD | PANEL_BUILDER | 2019-09-01 | 3
CUST-0568 | COMPANY_1245_0568 | PL | STANDARD | DISTRIBUTOR | 2013-02-01 | 5
CUST-0569 | COMPANY_5031_0569 | IN | GOLD | PANEL_BUILDER | 2012-12-01 | 6
CUST-0570 | COMPANY_6900_0570 | MX | STANDARD | END_USER | 2013-06-01 | 2
CUST-0571 | COMPANY_6331_0571 | ID | STANDARD | PANEL_BUILDER | 2013-01-01 | 2
CUST-0572 | COMPANY_7924_0572 | IT | STANDARD | END_USER | 2017-05-01 | 6
CUST-0573 | COMPANY_4199_0573 | ID | STANDARD | DISTRIBUTOR | 2021-04-01 | 5
CUST-0574 | COMPANY_5448_0574 | JP | STANDARD | DISTRIBUTOR | 2018-08-01 | 4
CUST-0575 | COMPANY_7350_0575 | AU | STANDARD | PANEL_BUILDER | 2023-08-01 | 4
CUST-0576 | COMPANY_6590_0576 | ID | STANDARD | PANEL_BUILDER | 2012-10-01 | 3
CUST-0577 | COMPANY_4846_0577 | ID | GOLD | DISTRIBUTOR | 2014-12-01 | 2
CUST-0578 | COMPANY_2163_0578 | US | STANDARD | EPC | 2015-01-01 | 1
CUST-0579 | COMPANY_5556_0579 | FR | STANDARD | END_USER | 2013-02-01 | 2
CUST-0580 | COMPANY_9455_0580 | MX | GOLD | DISTRIBUTOR | 2017-10-01 | 1
CUST-0581 | COMPANY_3894_0581 | IT | PLATINUM | PANEL_BUILDER | 2019-06-01 | 4
CUST-0582 | COMPANY_5772_0582 | TH | PLATINUM | END_USER | 2022-11-01 | 5
CUST-0583 | COMPANY_9158_0583 | VN | STANDARD | SYSTEM_INTEGRATOR | 2021-06-01 | 1
CUST-0584 | COMPANY_6811_0584 | IT | PLATINUM | SYSTEM_INTEGRATOR | 2025-03-01 | 5
CUST-0585 | COMPANY_7532_0585 | CN | STANDARD | DISTRIBUTOR | 2016-07-01 | 4
CUST-0586 | COMPANY_9567_0586 | IN | STANDARD | PANEL_BUILDER | 2025-03-01 | 1
CUST-0587 | COMPANY_5000_0587 | FR | STANDARD | EPC | 2022-11-01 | 3
CUST-0588 | COMPANY_6653_0588 | IT | STANDARD | DISTRIBUTOR | 2015-06-01 | 1
CUST-0589 | COMPANY_6256_0589 | PL | GOLD | PANEL_BUILDER | 2014-06-01 | 1
CUST-0590 | COMPANY_7758_0590 | GB | STANDARD | DISTRIBUTOR | 2022-06-01 | 6
CUST-0591 | COMPANY_5818_0591 | MX | GOLD | DISTRIBUTOR | 2019-12-01 | 5
CUST-0592 | COMPANY_8499_0592 | US | STANDARD | END_USER | 2020-06-01 | 4
CUST-0593 | COMPANY_9053_0593 | IT | GOLD | DISTRIBUTOR | 2021-10-01 | 1
CUST-0594 | COMPANY_1078_0594 | IN | STANDARD | PANEL_BUILDER | 2014-07-01 | 3
CUST-0595 | COMPANY_4504_0595 | TH | GOLD | DISTRIBUTOR | 2014-03-01 | 6
CUST-0596 | COMPANY_2024_0596 | TH | STANDARD | DISTRIBUTOR | 2015-04-01 | 5
CUST-0597 | COMPANY_1865_0597 | MX | PLATINUM | DISTRIBUTOR | 2025-08-01 | 3
CUST-0598 | COMPANY_5820_0598 | MX | STANDARD | PANEL_BUILDER | 2015-03-01 | 5
CUST-0599 | COMPANY_9909_0599 | ES | GOLD | END_USER | 2021-04-01 | 6
CUST-0600 | COMPANY_1337_0600 | DE | PLATINUM | EPC | 2019-04-01 | 3

## departments
dept_code | dept_name_ko | dept_name_en | level | scope
GCS_L1 | 글로벌 C/S 센터 | Global CS Center | L1 | 접수·분류·일반 문의·문서 송부
TS_LV | 저압기기 기술지원 | LV Distribution Technical Support | L2 | MCCB·ACB·ELCB·접촉기·계전기·계측기
TS_MV | 고압·배전반 기술지원 | MV & Switchgear Technical Support | L2 | VCB·고압 배전반
TS_TRF | 변압기 기술지원 | Transformer Engineering Support | L2 | 몰드·유입 변압기
TS_AUTO | 자동화 기술지원 | Automation Technical Support | L2 | 인버터·PLC·HMI
TS_ENERGY | 에너지솔루션 기술지원 | Energy Solutions Technical Support | L2 | ESS PCS·BMS·태양광 인버터·UPS
RND_FW | 펌웨어 개발 | Firmware R&D | L3 | 펌웨어 결함 분석·패치
QA_CLAIM | 품질보증/클레임 | Quality Assurance & Claim | L3 | 불량 원인 분석·클레임 판정
FIELD_SVC | 현장 서비스 | Field Service | L2 | 현장 출동·시운전·수리
CERT | 인증·규격 | Certification & Compliance | L2 | 인증서·시험성적서·규격 적합성
SALES_OPS | 해외영업 운영 | Overseas Sales Operations | L2 | 견적·가격·계약 조건
SCM | 주문·물류 | Order & Logistics (SCM) | L2 | 납기·출하·물류
WARRANTY_DESK | 보증·RMA 데스크 | Warranty & RMA Desk | L2 | 보증 판정·RMA 발행·교환

## sla_policy
sla_id | category | customer_tier | priority | first_response_hours | resolution_hours | clock | resolution_definition | at_risk_threshold | pause_rule
SLA-TECH_SPEC-PLATINUM-P1 | TECH_SPEC | PLATINUM | P1 | 1 | 24 | 24x7 calendar hours | 요청 사양에 대한 확정 답변 송부 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-TECH_SPEC-PLATINUM-P2 | TECH_SPEC | PLATINUM | P2 | 4 | 72 | 24x7 calendar hours | 요청 사양에 대한 확정 답변 송부 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-TECH_SPEC-PLATINUM-P3 | TECH_SPEC | PLATINUM | P3 | 8 | 120 | 24x7 calendar hours | 요청 사양에 대한 확정 답변 송부 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-TECH_SPEC-PLATINUM-P4 | TECH_SPEC | PLATINUM | P4 | 24 | 168 | 24x7 calendar hours | 요청 사양에 대한 확정 답변 송부 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-TECH_SPEC-GOLD-P1 | TECH_SPEC | GOLD | P1 | 2 | 48 | 24x7 calendar hours | 요청 사양에 대한 확정 답변 송부 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-TECH_SPEC-GOLD-P2 | TECH_SPEC | GOLD | P2 | 8 | 120 | 24x7 calendar hours | 요청 사양에 대한 확정 답변 송부 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-TECH_SPEC-GOLD-P3 | TECH_SPEC | GOLD | P3 | 16 | 168 | 24x7 calendar hours | 요청 사양에 대한 확정 답변 송부 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-TECH_SPEC-GOLD-P4 | TECH_SPEC | GOLD | P4 | 48 | 240 | 24x7 calendar hours | 요청 사양에 대한 확정 답변 송부 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-TECH_SPEC-STANDARD-P1 | TECH_SPEC | STANDARD | P1 | 4 | 72 | 24x7 calendar hours | 요청 사양에 대한 확정 답변 송부 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-TECH_SPEC-STANDARD-P2 | TECH_SPEC | STANDARD | P2 | 12 | 168 | 24x7 calendar hours | 요청 사양에 대한 확정 답변 송부 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-TECH_SPEC-STANDARD-P3 | TECH_SPEC | STANDARD | P3 | 24 | 240 | 24x7 calendar hours | 요청 사양에 대한 확정 답변 송부 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-TECH_SPEC-STANDARD-P4 | TECH_SPEC | STANDARD | P4 | 72 | 336 | 24x7 calendar hours | 요청 사양에 대한 확정 답변 송부 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-INSTALL-PLATINUM-P1 | INSTALL | PLATINUM | P1 | 1 | 24 | 24x7 calendar hours | 설치/시운전 이슈 해소 또는 현장 지원 일정 확정 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-INSTALL-PLATINUM-P2 | INSTALL | PLATINUM | P2 | 4 | 72 | 24x7 calendar hours | 설치/시운전 이슈 해소 또는 현장 지원 일정 확정 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-INSTALL-PLATINUM-P3 | INSTALL | PLATINUM | P3 | 8 | 120 | 24x7 calendar hours | 설치/시운전 이슈 해소 또는 현장 지원 일정 확정 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-INSTALL-PLATINUM-P4 | INSTALL | PLATINUM | P4 | 24 | 168 | 24x7 calendar hours | 설치/시운전 이슈 해소 또는 현장 지원 일정 확정 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-INSTALL-GOLD-P1 | INSTALL | GOLD | P1 | 2 | 48 | 24x7 calendar hours | 설치/시운전 이슈 해소 또는 현장 지원 일정 확정 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-INSTALL-GOLD-P2 | INSTALL | GOLD | P2 | 8 | 120 | 24x7 calendar hours | 설치/시운전 이슈 해소 또는 현장 지원 일정 확정 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-INSTALL-GOLD-P3 | INSTALL | GOLD | P3 | 16 | 168 | 24x7 calendar hours | 설치/시운전 이슈 해소 또는 현장 지원 일정 확정 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-INSTALL-GOLD-P4 | INSTALL | GOLD | P4 | 48 | 240 | 24x7 calendar hours | 설치/시운전 이슈 해소 또는 현장 지원 일정 확정 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-INSTALL-STANDARD-P1 | INSTALL | STANDARD | P1 | 4 | 72 | 24x7 calendar hours | 설치/시운전 이슈 해소 또는 현장 지원 일정 확정 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-INSTALL-STANDARD-P2 | INSTALL | STANDARD | P2 | 12 | 168 | 24x7 calendar hours | 설치/시운전 이슈 해소 또는 현장 지원 일정 확정 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-INSTALL-STANDARD-P3 | INSTALL | STANDARD | P3 | 24 | 240 | 24x7 calendar hours | 설치/시운전 이슈 해소 또는 현장 지원 일정 확정 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-INSTALL-STANDARD-P4 | INSTALL | STANDARD | P4 | 72 | 336 | 24x7 calendar hours | 설치/시운전 이슈 해소 또는 현장 지원 일정 확정 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-WARRANTY-PLATINUM-P1 | WARRANTY | PLATINUM | P1 | 1 | 36 | 24x7 calendar hours | 보증 적용 여부 판정 및 고객 통보 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-WARRANTY-PLATINUM-P2 | WARRANTY | PLATINUM | P2 | 4 | 108 | 24x7 calendar hours | 보증 적용 여부 판정 및 고객 통보 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-WARRANTY-PLATINUM-P3 | WARRANTY | PLATINUM | P3 | 8 | 180 | 24x7 calendar hours | 보증 적용 여부 판정 및 고객 통보 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-WARRANTY-PLATINUM-P4 | WARRANTY | PLATINUM | P4 | 24 | 252 | 24x7 calendar hours | 보증 적용 여부 판정 및 고객 통보 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-WARRANTY-GOLD-P1 | WARRANTY | GOLD | P1 | 2 | 72 | 24x7 calendar hours | 보증 적용 여부 판정 및 고객 통보 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-WARRANTY-GOLD-P2 | WARRANTY | GOLD | P2 | 8 | 180 | 24x7 calendar hours | 보증 적용 여부 판정 및 고객 통보 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-WARRANTY-GOLD-P3 | WARRANTY | GOLD | P3 | 16 | 252 | 24x7 calendar hours | 보증 적용 여부 판정 및 고객 통보 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-WARRANTY-GOLD-P4 | WARRANTY | GOLD | P4 | 48 | 360 | 24x7 calendar hours | 보증 적용 여부 판정 및 고객 통보 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-WARRANTY-STANDARD-P1 | WARRANTY | STANDARD | P1 | 4 | 108 | 24x7 calendar hours | 보증 적용 여부 판정 및 고객 통보 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-WARRANTY-STANDARD-P2 | WARRANTY | STANDARD | P2 | 12 | 252 | 24x7 calendar hours | 보증 적용 여부 판정 및 고객 통보 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-WARRANTY-STANDARD-P3 | WARRANTY | STANDARD | P3 | 24 | 360 | 24x7 calendar hours | 보증 적용 여부 판정 및 고객 통보 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-WARRANTY-STANDARD-P4 | WARRANTY | STANDARD | P4 | 72 | 504 | 24x7 calendar hours | 보증 적용 여부 판정 및 고객 통보 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-ORDER_LEAD-PLATINUM-P1 | ORDER_LEAD | PLATINUM | P1 | 1 | 12 | 24x7 calendar hours | 납기 확정 회신 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-ORDER_LEAD-PLATINUM-P2 | ORDER_LEAD | PLATINUM | P2 | 4 | 36 | 24x7 calendar hours | 납기 확정 회신 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-ORDER_LEAD-PLATINUM-P3 | ORDER_LEAD | PLATINUM | P3 | 8 | 60 | 24x7 calendar hours | 납기 확정 회신 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-ORDER_LEAD-PLATINUM-P4 | ORDER_LEAD | PLATINUM | P4 | 24 | 84 | 24x7 calendar hours | 납기 확정 회신 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-ORDER_LEAD-GOLD-P1 | ORDER_LEAD | GOLD | P1 | 2 | 24 | 24x7 calendar hours | 납기 확정 회신 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-ORDER_LEAD-GOLD-P2 | ORDER_LEAD | GOLD | P2 | 8 | 60 | 24x7 calendar hours | 납기 확정 회신 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-ORDER_LEAD-GOLD-P3 | ORDER_LEAD | GOLD | P3 | 16 | 84 | 24x7 calendar hours | 납기 확정 회신 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-ORDER_LEAD-GOLD-P4 | ORDER_LEAD | GOLD | P4 | 48 | 120 | 24x7 calendar hours | 납기 확정 회신 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-ORDER_LEAD-STANDARD-P1 | ORDER_LEAD | STANDARD | P1 | 4 | 36 | 24x7 calendar hours | 납기 확정 회신 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-ORDER_LEAD-STANDARD-P2 | ORDER_LEAD | STANDARD | P2 | 12 | 84 | 24x7 calendar hours | 납기 확정 회신 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-ORDER_LEAD-STANDARD-P3 | ORDER_LEAD | STANDARD | P3 | 24 | 120 | 24x7 calendar hours | 납기 확정 회신 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-ORDER_LEAD-STANDARD-P4 | ORDER_LEAD | STANDARD | P4 | 72 | 168 | 24x7 calendar hours | 납기 확정 회신 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-MANUAL-PLATINUM-P1 | MANUAL | PLATINUM | P1 | 1 | 12 | 24x7 calendar hours | 요청 문서 송부 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-MANUAL-PLATINUM-P2 | MANUAL | PLATINUM | P2 | 4 | 36 | 24x7 calendar hours | 요청 문서 송부 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-MANUAL-PLATINUM-P3 | MANUAL | PLATINUM | P3 | 8 | 60 | 24x7 calendar hours | 요청 문서 송부 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-MANUAL-PLATINUM-P4 | MANUAL | PLATINUM | P4 | 24 | 84 | 24x7 calendar hours | 요청 문서 송부 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-MANUAL-GOLD-P1 | MANUAL | GOLD | P1 | 2 | 24 | 24x7 calendar hours | 요청 문서 송부 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-MANUAL-GOLD-P2 | MANUAL | GOLD | P2 | 8 | 60 | 24x7 calendar hours | 요청 문서 송부 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-MANUAL-GOLD-P3 | MANUAL | GOLD | P3 | 16 | 84 | 24x7 calendar hours | 요청 문서 송부 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-MANUAL-GOLD-P4 | MANUAL | GOLD | P4 | 48 | 120 | 24x7 calendar hours | 요청 문서 송부 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-MANUAL-STANDARD-P1 | MANUAL | STANDARD | P1 | 4 | 36 | 24x7 calendar hours | 요청 문서 송부 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-MANUAL-STANDARD-P2 | MANUAL | STANDARD | P2 | 12 | 84 | 24x7 calendar hours | 요청 문서 송부 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-MANUAL-STANDARD-P3 | MANUAL | STANDARD | P3 | 24 | 120 | 24x7 calendar hours | 요청 문서 송부 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-MANUAL-STANDARD-P4 | MANUAL | STANDARD | P4 | 72 | 168 | 24x7 calendar hours | 요청 문서 송부 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-DEFECT-PLATINUM-P1 | DEFECT | PLATINUM | P1 | 1 | 24 | 24x7 calendar hours | 원인 규명 및 조치 완료 (현장 수리 포함, RMA 건은 RMA 발행 시점) | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-DEFECT-PLATINUM-P2 | DEFECT | PLATINUM | P2 | 4 | 72 | 24x7 calendar hours | 원인 규명 및 조치 완료 (현장 수리 포함, RMA 건은 RMA 발행 시점) | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-DEFECT-PLATINUM-P3 | DEFECT | PLATINUM | P3 | 8 | 120 | 24x7 calendar hours | 원인 규명 및 조치 완료 (현장 수리 포함, RMA 건은 RMA 발행 시점) | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-DEFECT-PLATINUM-P4 | DEFECT | PLATINUM | P4 | 24 | 168 | 24x7 calendar hours | 원인 규명 및 조치 완료 (현장 수리 포함, RMA 건은 RMA 발행 시점) | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-DEFECT-GOLD-P1 | DEFECT | GOLD | P1 | 2 | 48 | 24x7 calendar hours | 원인 규명 및 조치 완료 (현장 수리 포함, RMA 건은 RMA 발행 시점) | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-DEFECT-GOLD-P2 | DEFECT | GOLD | P2 | 8 | 120 | 24x7 calendar hours | 원인 규명 및 조치 완료 (현장 수리 포함, RMA 건은 RMA 발행 시점) | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-DEFECT-GOLD-P3 | DEFECT | GOLD | P3 | 16 | 168 | 24x7 calendar hours | 원인 규명 및 조치 완료 (현장 수리 포함, RMA 건은 RMA 발행 시점) | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-DEFECT-GOLD-P4 | DEFECT | GOLD | P4 | 48 | 240 | 24x7 calendar hours | 원인 규명 및 조치 완료 (현장 수리 포함, RMA 건은 RMA 발행 시점) | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-DEFECT-STANDARD-P1 | DEFECT | STANDARD | P1 | 4 | 72 | 24x7 calendar hours | 원인 규명 및 조치 완료 (현장 수리 포함, RMA 건은 RMA 발행 시점) | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-DEFECT-STANDARD-P2 | DEFECT | STANDARD | P2 | 12 | 168 | 24x7 calendar hours | 원인 규명 및 조치 완료 (현장 수리 포함, RMA 건은 RMA 발행 시점) | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-DEFECT-STANDARD-P3 | DEFECT | STANDARD | P3 | 24 | 240 | 24x7 calendar hours | 원인 규명 및 조치 완료 (현장 수리 포함, RMA 건은 RMA 발행 시점) | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-DEFECT-STANDARD-P4 | DEFECT | STANDARD | P4 | 72 | 336 | 24x7 calendar hours | 원인 규명 및 조치 완료 (현장 수리 포함, RMA 건은 RMA 발행 시점) | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-COMPLIANCE-PLATINUM-P1 | COMPLIANCE | PLATINUM | P1 | 1 | 24 | 24x7 calendar hours | 인증서·시험성적서·적합성 답변 송부 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-COMPLIANCE-PLATINUM-P2 | COMPLIANCE | PLATINUM | P2 | 4 | 72 | 24x7 calendar hours | 인증서·시험성적서·적합성 답변 송부 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-COMPLIANCE-PLATINUM-P3 | COMPLIANCE | PLATINUM | P3 | 8 | 120 | 24x7 calendar hours | 인증서·시험성적서·적합성 답변 송부 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-COMPLIANCE-PLATINUM-P4 | COMPLIANCE | PLATINUM | P4 | 24 | 168 | 24x7 calendar hours | 인증서·시험성적서·적합성 답변 송부 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-COMPLIANCE-GOLD-P1 | COMPLIANCE | GOLD | P1 | 2 | 48 | 24x7 calendar hours | 인증서·시험성적서·적합성 답변 송부 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-COMPLIANCE-GOLD-P2 | COMPLIANCE | GOLD | P2 | 8 | 120 | 24x7 calendar hours | 인증서·시험성적서·적합성 답변 송부 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-COMPLIANCE-GOLD-P3 | COMPLIANCE | GOLD | P3 | 16 | 168 | 24x7 calendar hours | 인증서·시험성적서·적합성 답변 송부 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-COMPLIANCE-GOLD-P4 | COMPLIANCE | GOLD | P4 | 48 | 240 | 24x7 calendar hours | 인증서·시험성적서·적합성 답변 송부 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-COMPLIANCE-STANDARD-P1 | COMPLIANCE | STANDARD | P1 | 4 | 72 | 24x7 calendar hours | 인증서·시험성적서·적합성 답변 송부 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-COMPLIANCE-STANDARD-P2 | COMPLIANCE | STANDARD | P2 | 12 | 168 | 24x7 calendar hours | 인증서·시험성적서·적합성 답변 송부 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-COMPLIANCE-STANDARD-P3 | COMPLIANCE | STANDARD | P3 | 24 | 240 | 24x7 calendar hours | 인증서·시험성적서·적합성 답변 송부 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-COMPLIANCE-STANDARD-P4 | COMPLIANCE | STANDARD | P4 | 72 | 336 | 24x7 calendar hours | 인증서·시험성적서·적합성 답변 송부 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-QUOTE-PLATINUM-P1 | QUOTE | PLATINUM | P1 | 1 | 24 | 24x7 calendar hours | 공식 견적서 발행 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-QUOTE-PLATINUM-P2 | QUOTE | PLATINUM | P2 | 4 | 72 | 24x7 calendar hours | 공식 견적서 발행 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-QUOTE-PLATINUM-P3 | QUOTE | PLATINUM | P3 | 8 | 120 | 24x7 calendar hours | 공식 견적서 발행 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-QUOTE-PLATINUM-P4 | QUOTE | PLATINUM | P4 | 24 | 168 | 24x7 calendar hours | 공식 견적서 발행 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-QUOTE-GOLD-P1 | QUOTE | GOLD | P1 | 2 | 48 | 24x7 calendar hours | 공식 견적서 발행 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-QUOTE-GOLD-P2 | QUOTE | GOLD | P2 | 8 | 120 | 24x7 calendar hours | 공식 견적서 발행 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-QUOTE-GOLD-P3 | QUOTE | GOLD | P3 | 16 | 168 | 24x7 calendar hours | 공식 견적서 발행 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-QUOTE-GOLD-P4 | QUOTE | GOLD | P4 | 48 | 240 | 24x7 calendar hours | 공식 견적서 발행 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-QUOTE-STANDARD-P1 | QUOTE | STANDARD | P1 | 4 | 72 | 24x7 calendar hours | 공식 견적서 발행 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-QUOTE-STANDARD-P2 | QUOTE | STANDARD | P2 | 12 | 168 | 24x7 calendar hours | 공식 견적서 발행 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-QUOTE-STANDARD-P3 | QUOTE | STANDARD | P3 | 24 | 240 | 24x7 calendar hours | 공식 견적서 발행 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-QUOTE-STANDARD-P4 | QUOTE | STANDARD | P4 | 72 | 336 | 24x7 calendar hours | 공식 견적서 발행 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-FW_UPDATE-PLATINUM-P1 | FW_UPDATE | PLATINUM | P1 | 1 | 24 | 24x7 calendar hours | 펌웨어 파일·절차 제공 및 적용 확인 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-FW_UPDATE-PLATINUM-P2 | FW_UPDATE | PLATINUM | P2 | 4 | 72 | 24x7 calendar hours | 펌웨어 파일·절차 제공 및 적용 확인 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-FW_UPDATE-PLATINUM-P3 | FW_UPDATE | PLATINUM | P3 | 8 | 120 | 24x7 calendar hours | 펌웨어 파일·절차 제공 및 적용 확인 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-FW_UPDATE-PLATINUM-P4 | FW_UPDATE | PLATINUM | P4 | 24 | 168 | 24x7 calendar hours | 펌웨어 파일·절차 제공 및 적용 확인 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-FW_UPDATE-GOLD-P1 | FW_UPDATE | GOLD | P1 | 2 | 48 | 24x7 calendar hours | 펌웨어 파일·절차 제공 및 적용 확인 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-FW_UPDATE-GOLD-P2 | FW_UPDATE | GOLD | P2 | 8 | 120 | 24x7 calendar hours | 펌웨어 파일·절차 제공 및 적용 확인 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-FW_UPDATE-GOLD-P3 | FW_UPDATE | GOLD | P3 | 16 | 168 | 24x7 calendar hours | 펌웨어 파일·절차 제공 및 적용 확인 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-FW_UPDATE-GOLD-P4 | FW_UPDATE | GOLD | P4 | 48 | 240 | 24x7 calendar hours | 펌웨어 파일·절차 제공 및 적용 확인 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-FW_UPDATE-STANDARD-P1 | FW_UPDATE | STANDARD | P1 | 4 | 72 | 24x7 calendar hours | 펌웨어 파일·절차 제공 및 적용 확인 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-FW_UPDATE-STANDARD-P2 | FW_UPDATE | STANDARD | P2 | 12 | 168 | 24x7 calendar hours | 펌웨어 파일·절차 제공 및 적용 확인 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-FW_UPDATE-STANDARD-P3 | FW_UPDATE | STANDARD | P3 | 24 | 240 | 24x7 calendar hours | 펌웨어 파일·절차 제공 및 적용 확인 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-FW_UPDATE-STANDARD-P4 | FW_UPDATE | STANDARD | P4 | 72 | 336 | 24x7 calendar hours | 펌웨어 파일·절차 제공 및 적용 확인 | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-RETURN-PLATINUM-P1 | RETURN | PLATINUM | P1 | 1 | 48 | 24x7 calendar hours | RMA 승인/반려 판정 (물리적 교환 완료는 별도) | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-RETURN-PLATINUM-P2 | RETURN | PLATINUM | P2 | 4 | 144 | 24x7 calendar hours | RMA 승인/반려 판정 (물리적 교환 완료는 별도) | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-RETURN-PLATINUM-P3 | RETURN | PLATINUM | P3 | 8 | 240 | 24x7 calendar hours | RMA 승인/반려 판정 (물리적 교환 완료는 별도) | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-RETURN-PLATINUM-P4 | RETURN | PLATINUM | P4 | 24 | 336 | 24x7 calendar hours | RMA 승인/반려 판정 (물리적 교환 완료는 별도) | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-RETURN-GOLD-P1 | RETURN | GOLD | P1 | 2 | 96 | 24x7 calendar hours | RMA 승인/반려 판정 (물리적 교환 완료는 별도) | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-RETURN-GOLD-P2 | RETURN | GOLD | P2 | 8 | 240 | 24x7 calendar hours | RMA 승인/반려 판정 (물리적 교환 완료는 별도) | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-RETURN-GOLD-P3 | RETURN | GOLD | P3 | 16 | 336 | 24x7 calendar hours | RMA 승인/반려 판정 (물리적 교환 완료는 별도) | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-RETURN-GOLD-P4 | RETURN | GOLD | P4 | 48 | 480 | 24x7 calendar hours | RMA 승인/반려 판정 (물리적 교환 완료는 별도) | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-RETURN-STANDARD-P1 | RETURN | STANDARD | P1 | 4 | 144 | 24x7 calendar hours | RMA 승인/반려 판정 (물리적 교환 완료는 별도) | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-RETURN-STANDARD-P2 | RETURN | STANDARD | P2 | 12 | 336 | 24x7 calendar hours | RMA 승인/반려 판정 (물리적 교환 완료는 별도) | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-RETURN-STANDARD-P3 | RETURN | STANDARD | P3 | 24 | 480 | 24x7 calendar hours | RMA 승인/반려 판정 (물리적 교환 완료는 별도) | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외
SLA-RETURN-STANDARD-P4 | RETURN | STANDARD | P4 | 72 | 672 | 24x7 calendar hours | RMA 승인/반려 판정 (물리적 교환 완료는 별도) | elapsed >= 75% of target | WAITING_CUSTOMER(추가정보 요청 후 고객 회신 대기) 시간은 SLA 경과시간에서 제외

## priority_rules
rule_id | order | condition | priority | priority_definition
PR-01 | 1 | urgency=SAFETY (모든 Category) | P1 | Critical — 안전 위험(발연·화재·감전·아크) 또는 설비 전체 정지
PR-02 | 2 | urgency=SITE_DOWN 이고 Category ∈ {DEFECT, INSTALL, FW_UPDATE} | P1 | Critical — 안전 위험(발연·화재·감전·아크) 또는 설비 전체 정지
PR-03 | 3 | urgency=SITE_DOWN 이고 Category ∈ {ORDER_LEAD, RETURN, WARRANTY} | P2 | High — 생산/운전에 영향, 시운전 중단, 반복 트립
PR-04 | 4 | urgency ∈ {PROD_IMPACT, COMMISSION} | P2 | High — 생산/운전에 영향, 시운전 중단, 반복 트립
PR-05 | 5 | Category ∈ {DEFECT, INSTALL, FW_UPDATE, WARRANTY, RETURN, ORDER_LEAD} | P3 | Normal — 운전 가능한 기술 문제, 일반 보증·반품·주문
PR-06 | 6 | urgency=DEADLINE (정보성 Category) | P3 | Normal — 운전 가능한 기술 문제, 일반 보증·반품·주문
PR-07 | 7 | 그 외 정보 요청 (TECH_SPEC, MANUAL, COMPLIANCE, QUOTE) | P4 | Low — 정보 요청(문서·사양·견적·인증), 기한 여유

## routing_rules
rule_id | family | category | rule_source | primary_dept | escalation_dept | escalation_condition
RT-LV_BREAKER-TECH_SPEC | LV_BREAKER | TECH_SPEC | CATEGORY_DEFAULT | TS_LV | CERT | 규격 해석·특수 사양 검토가 필요한 경우
RT-LV_BREAKER-INSTALL | LV_BREAKER | INSTALL | CATEGORY_DEFAULT | TS_LV | FIELD_SVC | P1/P2 이거나 현장 확인이 필요한 경우
RT-LV_BREAKER-WARRANTY | LV_BREAKER | WARRANTY | CATEGORY_DEFAULT | WARRANTY_DESK | QA_CLAIM | 보증 판정에 불량 원인 분석이 필요한 경우
RT-LV_BREAKER-ORDER_LEAD | LV_BREAKER | ORDER_LEAD | CATEGORY_DEFAULT | SCM | SALES_OPS | 고객이 계약 조건(가격·Incoterms) 변경을 요청한 경우
RT-LV_BREAKER-MANUAL | LV_BREAKER | MANUAL | CATEGORY_DEFAULT | GCS_L1 | TS_LV | 공개 문서로 답할 수 없는 기술 내용이 포함된 경우
RT-LV_BREAKER-DEFECT | LV_BREAKER | DEFECT | CATEGORY_DEFAULT | TS_LV | QA_CLAIM | P1 이거나 RMA/현장출동/펌웨어 결함이 확인된 경우 (대상 부서는 조치 유형별)
RT-LV_BREAKER-COMPLIANCE | LV_BREAKER | COMPLIANCE | CATEGORY_DEFAULT | CERT | TS_LV | 인증 범위 밖 시험·추가 성적서가 필요한 경우
RT-LV_BREAKER-QUOTE | LV_BREAKER | QUOTE | CATEGORY_DEFAULT | SALES_OPS | TS_LV | 표준 외 사양·커스터마이징이 필요한 경우
RT-LV_BREAKER-FW_UPDATE | LV_BREAKER | FW_UPDATE | CATEGORY_DEFAULT | TS_LV | RND_FW | 업데이트 실패·신규 결함 의심인 경우
RT-LV_BREAKER-RETURN | LV_BREAKER | RETURN | CATEGORY_DEFAULT | WARRANTY_DESK | QA_CLAIM | 불량 반품(DOA·품질)인 경우. 단순 오배송·변심은 SCM
RT-MV_EQUIP-TECH_SPEC | MV_EQUIP | TECH_SPEC | CATEGORY_DEFAULT | TS_MV | CERT | 규격 해석·특수 사양 검토가 필요한 경우
RT-MV_EQUIP-INSTALL | MV_EQUIP | INSTALL | FAMILY_OVERRIDE | FIELD_SVC | TS_MV | 고압기기 설치·시운전은 현장 서비스가 1차 담당 (감독 필수)
RT-MV_EQUIP-WARRANTY | MV_EQUIP | WARRANTY | CATEGORY_DEFAULT | WARRANTY_DESK | QA_CLAIM | 보증 판정에 불량 원인 분석이 필요한 경우
RT-MV_EQUIP-ORDER_LEAD | MV_EQUIP | ORDER_LEAD | CATEGORY_DEFAULT | SCM | SALES_OPS | 고객이 계약 조건(가격·Incoterms) 변경을 요청한 경우
RT-MV_EQUIP-MANUAL | MV_EQUIP | MANUAL | CATEGORY_DEFAULT | GCS_L1 | TS_MV | 공개 문서로 답할 수 없는 기술 내용이 포함된 경우
RT-MV_EQUIP-DEFECT | MV_EQUIP | DEFECT | FAMILY_OVERRIDE | TS_MV | FIELD_SVC | 현장 확인이 필요한 경우
RT-MV_EQUIP-COMPLIANCE | MV_EQUIP | COMPLIANCE | CATEGORY_DEFAULT | CERT | TS_MV | 인증 범위 밖 시험·추가 성적서가 필요한 경우
RT-MV_EQUIP-QUOTE | MV_EQUIP | QUOTE | CATEGORY_DEFAULT | SALES_OPS | TS_MV | 표준 외 사양·커스터마이징이 필요한 경우
RT-MV_EQUIP-RETURN | MV_EQUIP | RETURN | CATEGORY_DEFAULT | WARRANTY_DESK | QA_CLAIM | 불량 반품(DOA·품질)인 경우. 단순 오배송·변심은 SCM
RT-CONTROL-TECH_SPEC | CONTROL | TECH_SPEC | CATEGORY_DEFAULT | TS_LV | CERT | 규격 해석·특수 사양 검토가 필요한 경우
RT-CONTROL-INSTALL | CONTROL | INSTALL | CATEGORY_DEFAULT | TS_LV | FIELD_SVC | P1/P2 이거나 현장 확인이 필요한 경우
RT-CONTROL-WARRANTY | CONTROL | WARRANTY | CATEGORY_DEFAULT | WARRANTY_DESK | QA_CLAIM | 보증 판정에 불량 원인 분석이 필요한 경우
RT-CONTROL-ORDER_LEAD | CONTROL | ORDER_LEAD | CATEGORY_DEFAULT | SCM | SALES_OPS | 고객이 계약 조건(가격·Incoterms) 변경을 요청한 경우
RT-CONTROL-MANUAL | CONTROL | MANUAL | CATEGORY_DEFAULT | GCS_L1 | TS_LV | 공개 문서로 답할 수 없는 기술 내용이 포함된 경우
RT-CONTROL-DEFECT | CONTROL | DEFECT | CATEGORY_DEFAULT | TS_LV | QA_CLAIM | P1 이거나 RMA/현장출동/펌웨어 결함이 확인된 경우 (대상 부서는 조치 유형별)
RT-CONTROL-COMPLIANCE | CONTROL | COMPLIANCE | CATEGORY_DEFAULT | CERT | TS_LV | 인증 범위 밖 시험·추가 성적서가 필요한 경우
RT-CONTROL-QUOTE | CONTROL | QUOTE | CATEGORY_DEFAULT | SALES_OPS | TS_LV | 표준 외 사양·커스터마이징이 필요한 경우
RT-CONTROL-RETURN | CONTROL | RETURN | CATEGORY_DEFAULT | WARRANTY_DESK | QA_CLAIM | 불량 반품(DOA·품질)인 경우. 단순 오배송·변심은 SCM
RT-DRIVE-TECH_SPEC | DRIVE | TECH_SPEC | CATEGORY_DEFAULT | TS_AUTO | CERT | 규격 해석·특수 사양 검토가 필요한 경우
RT-DRIVE-INSTALL | DRIVE | INSTALL | CATEGORY_DEFAULT | TS_AUTO | FIELD_SVC | P1/P2 이거나 현장 확인이 필요한 경우
RT-DRIVE-WARRANTY | DRIVE | WARRANTY | CATEGORY_DEFAULT | WARRANTY_DESK | QA_CLAIM | 보증 판정에 불량 원인 분석이 필요한 경우
RT-DRIVE-ORDER_LEAD | DRIVE | ORDER_LEAD | CATEGORY_DEFAULT | SCM | SALES_OPS | 고객이 계약 조건(가격·Incoterms) 변경을 요청한 경우
RT-DRIVE-MANUAL | DRIVE | MANUAL | CATEGORY_DEFAULT | GCS_L1 | TS_AUTO | 공개 문서로 답할 수 없는 기술 내용이 포함된 경우
RT-DRIVE-DEFECT | DRIVE | DEFECT | CATEGORY_DEFAULT | TS_AUTO | QA_CLAIM | P1 이거나 RMA/현장출동/펌웨어 결함이 확인된 경우 (대상 부서는 조치 유형별)
RT-DRIVE-COMPLIANCE | DRIVE | COMPLIANCE | CATEGORY_DEFAULT | CERT | TS_AUTO | 인증 범위 밖 시험·추가 성적서가 필요한 경우
RT-DRIVE-QUOTE | DRIVE | QUOTE | CATEGORY_DEFAULT | SALES_OPS | TS_AUTO | 표준 외 사양·커스터마이징이 필요한 경우
RT-DRIVE-FW_UPDATE | DRIVE | FW_UPDATE | CATEGORY_DEFAULT | TS_AUTO | RND_FW | 업데이트 실패·신규 결함 의심인 경우
RT-DRIVE-RETURN | DRIVE | RETURN | CATEGORY_DEFAULT | WARRANTY_DESK | QA_CLAIM | 불량 반품(DOA·품질)인 경우. 단순 오배송·변심은 SCM
RT-PLC-TECH_SPEC | PLC | TECH_SPEC | CATEGORY_DEFAULT | TS_AUTO | CERT | 규격 해석·특수 사양 검토가 필요한 경우
RT-PLC-INSTALL | PLC | INSTALL | CATEGORY_DEFAULT | TS_AUTO | FIELD_SVC | P1/P2 이거나 현장 확인이 필요한 경우
RT-PLC-WARRANTY | PLC | WARRANTY | CATEGORY_DEFAULT | WARRANTY_DESK | QA_CLAIM | 보증 판정에 불량 원인 분석이 필요한 경우
RT-PLC-ORDER_LEAD | PLC | ORDER_LEAD | CATEGORY_DEFAULT | SCM | SALES_OPS | 고객이 계약 조건(가격·Incoterms) 변경을 요청한 경우
RT-PLC-MANUAL | PLC | MANUAL | CATEGORY_DEFAULT | GCS_L1 | TS_AUTO | 공개 문서로 답할 수 없는 기술 내용이 포함된 경우
RT-PLC-DEFECT | PLC | DEFECT | CATEGORY_DEFAULT | TS_AUTO | QA_CLAIM | P1 이거나 RMA/현장출동/펌웨어 결함이 확인된 경우 (대상 부서는 조치 유형별)
RT-PLC-COMPLIANCE | PLC | COMPLIANCE | CATEGORY_DEFAULT | CERT | TS_AUTO | 인증 범위 밖 시험·추가 성적서가 필요한 경우
RT-PLC-QUOTE | PLC | QUOTE | CATEGORY_DEFAULT | SALES_OPS | TS_AUTO | 표준 외 사양·커스터마이징이 필요한 경우
RT-PLC-FW_UPDATE | PLC | FW_UPDATE | CATEGORY_DEFAULT | TS_AUTO | RND_FW | 업데이트 실패·신규 결함 의심인 경우
RT-PLC-RETURN | PLC | RETURN | CATEGORY_DEFAULT | WARRANTY_DESK | QA_CLAIM | 불량 반품(DOA·품질)인 경우. 단순 오배송·변심은 SCM
RT-HMI-TECH_SPEC | HMI | TECH_SPEC | CATEGORY_DEFAULT | TS_AUTO | CERT | 규격 해석·특수 사양 검토가 필요한 경우
RT-HMI-INSTALL | HMI | INSTALL | CATEGORY_DEFAULT | TS_AUTO | FIELD_SVC | P1/P2 이거나 현장 확인이 필요한 경우
RT-HMI-WARRANTY | HMI | WARRANTY | CATEGORY_DEFAULT | WARRANTY_DESK | QA_CLAIM | 보증 판정에 불량 원인 분석이 필요한 경우
RT-HMI-ORDER_LEAD | HMI | ORDER_LEAD | CATEGORY_DEFAULT | SCM | SALES_OPS | 고객이 계약 조건(가격·Incoterms) 변경을 요청한 경우
RT-HMI-MANUAL | HMI | MANUAL | CATEGORY_DEFAULT | GCS_L1 | TS_AUTO | 공개 문서로 답할 수 없는 기술 내용이 포함된 경우
RT-HMI-DEFECT | HMI | DEFECT | CATEGORY_DEFAULT | TS_AUTO | QA_CLAIM | P1 이거나 RMA/현장출동/펌웨어 결함이 확인된 경우 (대상 부서는 조치 유형별)
RT-HMI-COMPLIANCE | HMI | COMPLIANCE | CATEGORY_DEFAULT | CERT | TS_AUTO | 인증 범위 밖 시험·추가 성적서가 필요한 경우
RT-HMI-QUOTE | HMI | QUOTE | CATEGORY_DEFAULT | SALES_OPS | TS_AUTO | 표준 외 사양·커스터마이징이 필요한 경우
RT-HMI-FW_UPDATE | HMI | FW_UPDATE | CATEGORY_DEFAULT | TS_AUTO | RND_FW | 업데이트 실패·신규 결함 의심인 경우
RT-HMI-RETURN | HMI | RETURN | CATEGORY_DEFAULT | WARRANTY_DESK | QA_CLAIM | 불량 반품(DOA·품질)인 경우. 단순 오배송·변심은 SCM
RT-TRANSFORMER-TECH_SPEC | TRANSFORMER | TECH_SPEC | CATEGORY_DEFAULT | TS_TRF | CERT | 규격 해석·특수 사양 검토가 필요한 경우
RT-TRANSFORMER-INSTALL | TRANSFORMER | INSTALL | FAMILY_OVERRIDE | FIELD_SVC | TS_TRF | 변압기 설치·시운전은 현장 서비스가 1차 담당
RT-TRANSFORMER-WARRANTY | TRANSFORMER | WARRANTY | CATEGORY_DEFAULT | WARRANTY_DESK | QA_CLAIM | 보증 판정에 불량 원인 분석이 필요한 경우
RT-TRANSFORMER-ORDER_LEAD | TRANSFORMER | ORDER_LEAD | CATEGORY_DEFAULT | SCM | SALES_OPS | 고객이 계약 조건(가격·Incoterms) 변경을 요청한 경우
RT-TRANSFORMER-MANUAL | TRANSFORMER | MANUAL | CATEGORY_DEFAULT | GCS_L1 | TS_TRF | 공개 문서로 답할 수 없는 기술 내용이 포함된 경우
RT-TRANSFORMER-DEFECT | TRANSFORMER | DEFECT | FAMILY_OVERRIDE | TS_TRF | FIELD_SVC | 현장 확인(DGA·IR 측정)이 필요한 경우
RT-TRANSFORMER-COMPLIANCE | TRANSFORMER | COMPLIANCE | CATEGORY_DEFAULT | CERT | TS_TRF | 인증 범위 밖 시험·추가 성적서가 필요한 경우
RT-TRANSFORMER-QUOTE | TRANSFORMER | QUOTE | CATEGORY_DEFAULT | SALES_OPS | TS_TRF | 표준 외 사양·커스터마이징이 필요한 경우
RT-TRANSFORMER-RETURN | TRANSFORMER | RETURN | CATEGORY_DEFAULT | WARRANTY_DESK | QA_CLAIM | 불량 반품(DOA·품질)인 경우. 단순 오배송·변심은 SCM
RT-METER-TECH_SPEC | METER | TECH_SPEC | CATEGORY_DEFAULT | TS_LV | CERT | 규격 해석·특수 사양 검토가 필요한 경우
RT-METER-INSTALL | METER | INSTALL | CATEGORY_DEFAULT | TS_LV | FIELD_SVC | P1/P2 이거나 현장 확인이 필요한 경우
RT-METER-WARRANTY | METER | WARRANTY | CATEGORY_DEFAULT | WARRANTY_DESK | QA_CLAIM | 보증 판정에 불량 원인 분석이 필요한 경우
RT-METER-ORDER_LEAD | METER | ORDER_LEAD | CATEGORY_DEFAULT | SCM | SALES_OPS | 고객이 계약 조건(가격·Incoterms) 변경을 요청한 경우
RT-METER-MANUAL | METER | MANUAL | CATEGORY_DEFAULT | GCS_L1 | TS_LV | 공개 문서로 답할 수 없는 기술 내용이 포함된 경우
RT-METER-DEFECT | METER | DEFECT | CATEGORY_DEFAULT | TS_LV | QA_CLAIM | P1 이거나 RMA/현장출동/펌웨어 결함이 확인된 경우 (대상 부서는 조치 유형별)
RT-METER-COMPLIANCE | METER | COMPLIANCE | CATEGORY_DEFAULT | CERT | TS_LV | 인증 범위 밖 시험·추가 성적서가 필요한 경우
RT-METER-QUOTE | METER | QUOTE | CATEGORY_DEFAULT | SALES_OPS | TS_LV | 표준 외 사양·커스터마이징이 필요한 경우
RT-METER-FW_UPDATE | METER | FW_UPDATE | CATEGORY_DEFAULT | TS_LV | RND_FW | 업데이트 실패·신규 결함 의심인 경우
RT-METER-RETURN | METER | RETURN | CATEGORY_DEFAULT | WARRANTY_DESK | QA_CLAIM | 불량 반품(DOA·품질)인 경우. 단순 오배송·변심은 SCM
RT-ESS-TECH_SPEC | ESS | TECH_SPEC | CATEGORY_DEFAULT | TS_ENERGY | CERT | 규격 해석·특수 사양 검토가 필요한 경우
RT-ESS-INSTALL | ESS | INSTALL | CATEGORY_DEFAULT | TS_ENERGY | FIELD_SVC | P1/P2 이거나 현장 확인이 필요한 경우
RT-ESS-WARRANTY | ESS | WARRANTY | CATEGORY_DEFAULT | WARRANTY_DESK | QA_CLAIM | 보증 판정에 불량 원인 분석이 필요한 경우
RT-ESS-ORDER_LEAD | ESS | ORDER_LEAD | CATEGORY_DEFAULT | SCM | SALES_OPS | 고객이 계약 조건(가격·Incoterms) 변경을 요청한 경우
RT-ESS-MANUAL | ESS | MANUAL | CATEGORY_DEFAULT | GCS_L1 | TS_ENERGY | 공개 문서로 답할 수 없는 기술 내용이 포함된 경우
RT-ESS-DEFECT | ESS | DEFECT | FAMILY_OVERRIDE | TS_ENERGY | FIELD_SVC | P1(안전) 또는 배터리 모듈 교체가 필요한 경우 현장 서비스
RT-ESS-COMPLIANCE | ESS | COMPLIANCE | CATEGORY_DEFAULT | CERT | TS_ENERGY | 인증 범위 밖 시험·추가 성적서가 필요한 경우
RT-ESS-QUOTE | ESS | QUOTE | CATEGORY_DEFAULT | SALES_OPS | TS_ENERGY | 표준 외 사양·커스터마이징이 필요한 경우
RT-ESS-FW_UPDATE | ESS | FW_UPDATE | CATEGORY_DEFAULT | TS_ENERGY | RND_FW | 업데이트 실패·신규 결함 의심인 경우
RT-ESS-RETURN | ESS | RETURN | CATEGORY_DEFAULT | WARRANTY_DESK | QA_CLAIM | 불량 반품(DOA·품질)인 경우. 단순 오배송·변심은 SCM
RT-PV-TECH_SPEC | PV | TECH_SPEC | CATEGORY_DEFAULT | TS_ENERGY | CERT | 규격 해석·특수 사양 검토가 필요한 경우
RT-PV-INSTALL | PV | INSTALL | CATEGORY_DEFAULT | TS_ENERGY | FIELD_SVC | P1/P2 이거나 현장 확인이 필요한 경우
RT-PV-WARRANTY | PV | WARRANTY | CATEGORY_DEFAULT | WARRANTY_DESK | QA_CLAIM | 보증 판정에 불량 원인 분석이 필요한 경우
RT-PV-ORDER_LEAD | PV | ORDER_LEAD | CATEGORY_DEFAULT | SCM | SALES_OPS | 고객이 계약 조건(가격·Incoterms) 변경을 요청한 경우
RT-PV-MANUAL | PV | MANUAL | CATEGORY_DEFAULT | GCS_L1 | TS_ENERGY | 공개 문서로 답할 수 없는 기술 내용이 포함된 경우
RT-PV-DEFECT | PV | DEFECT | CATEGORY_DEFAULT | TS_ENERGY | QA_CLAIM | P1 이거나 RMA/현장출동/펌웨어 결함이 확인된 경우 (대상 부서는 조치 유형별)
RT-PV-COMPLIANCE | PV | COMPLIANCE | CATEGORY_DEFAULT | CERT | TS_ENERGY | 인증 범위 밖 시험·추가 성적서가 필요한 경우
RT-PV-QUOTE | PV | QUOTE | CATEGORY_DEFAULT | SALES_OPS | TS_ENERGY | 표준 외 사양·커스터마이징이 필요한 경우
RT-PV-FW_UPDATE | PV | FW_UPDATE | CATEGORY_DEFAULT | TS_ENERGY | RND_FW | 업데이트 실패·신규 결함 의심인 경우
RT-PV-RETURN | PV | RETURN | CATEGORY_DEFAULT | WARRANTY_DESK | QA_CLAIM | 불량 반품(DOA·품질)인 경우. 단순 오배송·변심은 SCM
RT-UPS-TECH_SPEC | UPS | TECH_SPEC | CATEGORY_DEFAULT | TS_ENERGY | CERT | 규격 해석·특수 사양 검토가 필요한 경우
RT-UPS-INSTALL | UPS | INSTALL | CATEGORY_DEFAULT | TS_ENERGY | FIELD_SVC | P1/P2 이거나 현장 확인이 필요한 경우
RT-UPS-WARRANTY | UPS | WARRANTY | CATEGORY_DEFAULT | WARRANTY_DESK | QA_CLAIM | 보증 판정에 불량 원인 분석이 필요한 경우
RT-UPS-ORDER_LEAD | UPS | ORDER_LEAD | CATEGORY_DEFAULT | SCM | SALES_OPS | 고객이 계약 조건(가격·Incoterms) 변경을 요청한 경우
RT-UPS-MANUAL | UPS | MANUAL | CATEGORY_DEFAULT | GCS_L1 | TS_ENERGY | 공개 문서로 답할 수 없는 기술 내용이 포함된 경우
RT-UPS-DEFECT | UPS | DEFECT | CATEGORY_DEFAULT | TS_ENERGY | QA_CLAIM | P1 이거나 RMA/현장출동/펌웨어 결함이 확인된 경우 (대상 부서는 조치 유형별)
RT-UPS-COMPLIANCE | UPS | COMPLIANCE | CATEGORY_DEFAULT | CERT | TS_ENERGY | 인증 범위 밖 시험·추가 성적서가 필요한 경우
RT-UPS-QUOTE | UPS | QUOTE | CATEGORY_DEFAULT | SALES_OPS | TS_ENERGY | 표준 외 사양·커스터마이징이 필요한 경우
RT-UPS-FW_UPDATE | UPS | FW_UPDATE | CATEGORY_DEFAULT | TS_ENERGY | RND_FW | 업데이트 실패·신규 결함 의심인 경우
RT-UPS-RETURN | UPS | RETURN | CATEGORY_DEFAULT | WARRANTY_DESK | QA_CLAIM | 불량 반품(DOA·품질)인 경우. 단순 오배송·변심은 SCM
RT-ALL-RETURN-NON_DEFECT | ALL | RETURN | SUBTYPE_OVERRIDE | SCM | SALES_OPS | 오배송·주문 착오·잉여 반품 — 크레딧/재출하 조건 협의 시 해외영업
RT-ESC-DEFECT-RMA | ALL | DEFECT | ESCALATION | (제품군 기술지원) | QA_CLAIM | DEFECT 조치 유형 = RMA
RT-ESC-DEFECT-ONSITE | ALL | DEFECT | ESCALATION | (제품군 기술지원) | FIELD_SVC | DEFECT 조치 유형 = ONSITE
RT-ESC-DEFECT-SAFETY | ALL | DEFECT | ESCALATION | (제품군 기술지원) | FIELD_SVC | DEFECT 조치 유형 = SAFETY

## required_info
family | category | required_fields | blocking_fields | field_labels
LV_BREAKER | TECH_SPEC | product_model;application | product_model | Product model / ordering code;Application (voltage, load, duty)
LV_BREAKER | INSTALL | product_model;serial_no;site_condition;wiring_diagram | product_model;site_condition | Product model / ordering code;Serial number (nameplate);Site condition (ambient temperature, altitude, humidity);Wiring / single-line diagram
LV_BREAKER | WARRANTY | serial_no;purchase_doc;install_date;failure_description;photos | serial_no;purchase_doc | Serial number (nameplate);PO or invoice number;Installation / commissioning date;Failure description and occurrence time;Photos of product and nameplate
LV_BREAKER | ORDER_LEAD | po_number;product_model;quantity;required_date | po_number | PO number;Product model / ordering code;Quantity;Required delivery date
LV_BREAKER | MANUAL | product_model;document_type | product_model | Product model / ordering code;Document type requested
LV_BREAKER | DEFECT | product_model;serial_no;error_code;operating_condition;photos;load_profile | serial_no;error_code | Product model / ordering code;Serial number (nameplate);Error code or symptom displayed;Operating condition at failure (load, speed, temperature);Photos of product and nameplate;Load current / temperature records
LV_BREAKER | COMPLIANCE | product_model;target_standard;target_country | target_standard | Product model / ordering code;Required standard / certificate;Destination country / market
LV_BREAKER | QUOTE | product_model;quantity;incoterms;required_date | quantity;incoterms | Product model / ordering code;Quantity;Incoterms and delivery destination;Required delivery date
LV_BREAKER | FW_UPDATE | product_model;serial_no;current_fw;tool_version | current_fw | Product model / ordering code;Serial number (nameplate);Current firmware version;Engineering tool / loader version
LV_BREAKER | RETURN | purchase_doc;serial_no;return_reason;photos;packaging_condition | purchase_doc;return_reason | PO or invoice number;Serial number (nameplate);Reason for return;Photos of product and nameplate;Packaging condition on arrival
MV_EQUIP | TECH_SPEC | product_model;application | product_model | Product model / ordering code;Application (voltage, load, duty)
MV_EQUIP | INSTALL | product_model;serial_no;site_condition;wiring_diagram | product_model;site_condition | Product model / ordering code;Serial number (nameplate);Site condition (ambient temperature, altitude, humidity);Wiring / single-line diagram
MV_EQUIP | WARRANTY | serial_no;purchase_doc;install_date;failure_description;photos | serial_no;purchase_doc | Serial number (nameplate);PO or invoice number;Installation / commissioning date;Failure description and occurrence time;Photos of product and nameplate
MV_EQUIP | ORDER_LEAD | po_number;product_model;quantity;required_date | po_number | PO number;Product model / ordering code;Quantity;Required delivery date
MV_EQUIP | MANUAL | product_model;document_type | product_model | Product model / ordering code;Document type requested
MV_EQUIP | DEFECT | product_model;serial_no;error_code;operating_condition;photos | serial_no;error_code | Product model / ordering code;Serial number (nameplate);Error code or symptom displayed;Operating condition at failure (load, speed, temperature);Photos of product and nameplate
MV_EQUIP | COMPLIANCE | product_model;target_standard;target_country | target_standard | Product model / ordering code;Required standard / certificate;Destination country / market
MV_EQUIP | QUOTE | product_model;quantity;incoterms;required_date | quantity;incoterms | Product model / ordering code;Quantity;Incoterms and delivery destination;Required delivery date
MV_EQUIP | FW_UPDATE | product_model;serial_no;current_fw;tool_version | current_fw | Product model / ordering code;Serial number (nameplate);Current firmware version;Engineering tool / loader version
MV_EQUIP | RETURN | purchase_doc;serial_no;return_reason;photos;packaging_condition | purchase_doc;return_reason | PO or invoice number;Serial number (nameplate);Reason for return;Photos of product and nameplate;Packaging condition on arrival
CONTROL | TECH_SPEC | product_model;application | product_model | Product model / ordering code;Application (voltage, load, duty)
CONTROL | INSTALL | product_model;serial_no;site_condition;wiring_diagram | product_model;site_condition | Product model / ordering code;Serial number (nameplate);Site condition (ambient temperature, altitude, humidity);Wiring / single-line diagram
CONTROL | WARRANTY | serial_no;purchase_doc;install_date;failure_description;photos | serial_no;purchase_doc | Serial number (nameplate);PO or invoice number;Installation / commissioning date;Failure description and occurrence time;Photos of product and nameplate
CONTROL | ORDER_LEAD | po_number;product_model;quantity;required_date | po_number | PO number;Product model / ordering code;Quantity;Required delivery date
CONTROL | MANUAL | product_model;document_type | product_model | Product model / ordering code;Document type requested
CONTROL | DEFECT | product_model;serial_no;error_code;operating_condition;photos | serial_no;error_code | Product model / ordering code;Serial number (nameplate);Error code or symptom displayed;Operating condition at failure (load, speed, temperature);Photos of product and nameplate
CONTROL | COMPLIANCE | product_model;target_standard;target_country | target_standard | Product model / ordering code;Required standard / certificate;Destination country / market
CONTROL | QUOTE | product_model;quantity;incoterms;required_date | quantity;incoterms | Product model / ordering code;Quantity;Incoterms and delivery destination;Required delivery date
CONTROL | FW_UPDATE | product_model;serial_no;current_fw;tool_version | current_fw | Product model / ordering code;Serial number (nameplate);Current firmware version;Engineering tool / loader version
CONTROL | RETURN | purchase_doc;serial_no;return_reason;photos;packaging_condition | purchase_doc;return_reason | PO or invoice number;Serial number (nameplate);Reason for return;Photos of product and nameplate;Packaging condition on arrival
DRIVE | TECH_SPEC | product_model;application | product_model | Product model / ordering code;Application (voltage, load, duty)
DRIVE | INSTALL | product_model;serial_no;site_condition;wiring_diagram;motor_nameplate | product_model;site_condition | Product model / ordering code;Serial number (nameplate);Site condition (ambient temperature, altitude, humidity);Wiring / single-line diagram;Motor nameplate data
DRIVE | WARRANTY | serial_no;purchase_doc;install_date;failure_description;photos | serial_no;purchase_doc | Serial number (nameplate);PO or invoice number;Installation / commissioning date;Failure description and occurrence time;Photos of product and nameplate
DRIVE | ORDER_LEAD | po_number;product_model;quantity;required_date | po_number | PO number;Product model / ordering code;Quantity;Required delivery date
DRIVE | MANUAL | product_model;document_type | product_model | Product model / ordering code;Document type requested
DRIVE | DEFECT | product_model;serial_no;error_code;operating_condition;photos;logs;parameter_backup;motor_nameplate | serial_no;error_code | Product model / ordering code;Serial number (nameplate);Error code or symptom displayed;Operating condition at failure (load, speed, temperature);Photos of product and nameplate;Event / trip log export;Parameter backup file;Motor nameplate data
DRIVE | COMPLIANCE | product_model;target_standard;target_country | target_standard | Product model / ordering code;Required standard / certificate;Destination country / market
DRIVE | QUOTE | product_model;quantity;incoterms;required_date | quantity;incoterms | Product model / ordering code;Quantity;Incoterms and delivery destination;Required delivery date
DRIVE | FW_UPDATE | product_model;serial_no;current_fw;tool_version | current_fw | Product model / ordering code;Serial number (nameplate);Current firmware version;Engineering tool / loader version
DRIVE | RETURN | purchase_doc;serial_no;return_reason;photos;packaging_condition | purchase_doc;return_reason | PO or invoice number;Serial number (nameplate);Reason for return;Photos of product and nameplate;Packaging condition on arrival
PLC | TECH_SPEC | product_model;application | product_model | Product model / ordering code;Application (voltage, load, duty)
PLC | INSTALL | product_model;serial_no;site_condition;wiring_diagram | product_model;site_condition | Product model / ordering code;Serial number (nameplate);Site condition (ambient temperature, altitude, humidity);Wiring / single-line diagram
PLC | WARRANTY | serial_no;purchase_doc;install_date;failure_description;photos | serial_no;purchase_doc | Serial number (nameplate);PO or invoice number;Installation / commissioning date;Failure description and occurrence time;Photos of product and nameplate
PLC | ORDER_LEAD | po_number;product_model;quantity;required_date | po_number | PO number;Product model / ordering code;Quantity;Required delivery date
PLC | MANUAL | product_model;document_type | product_model | Product model / ordering code;Document type requested
PLC | DEFECT | product_model;serial_no;error_code;operating_condition;photos;logs;program_backup | serial_no;error_code | Product model / ordering code;Serial number (nameplate);Error code or symptom displayed;Operating condition at failure (load, speed, temperature);Photos of product and nameplate;Event / trip log export;PLC/HMI project backup
PLC | COMPLIANCE | product_model;target_standard;target_country | target_standard | Product model / ordering code;Required standard / certificate;Destination country / market
PLC | QUOTE | product_model;quantity;incoterms;required_date | quantity;incoterms | Product model / ordering code;Quantity;Incoterms and delivery destination;Required delivery date
PLC | FW_UPDATE | product_model;serial_no;current_fw;tool_version;program_backup | current_fw | Product model / ordering code;Serial number (nameplate);Current firmware version;Engineering tool / loader version;PLC/HMI project backup
PLC | RETURN | purchase_doc;serial_no;return_reason;photos;packaging_condition | purchase_doc;return_reason | PO or invoice number;Serial number (nameplate);Reason for return;Photos of product and nameplate;Packaging condition on arrival
HMI | TECH_SPEC | product_model;application | product_model | Product model / ordering code;Application (voltage, load, duty)
HMI | INSTALL | product_model;serial_no;site_condition;wiring_diagram | product_model;site_condition | Product model / ordering code;Serial number (nameplate);Site condition (ambient temperature, altitude, humidity);Wiring / single-line diagram
HMI | WARRANTY | serial_no;purchase_doc;install_date;failure_description;photos | serial_no;purchase_doc | Serial number (nameplate);PO or invoice number;Installation / commissioning date;Failure description and occurrence time;Photos of product and nameplate
HMI | ORDER_LEAD | po_number;product_model;quantity;required_date | po_number | PO number;Product model / ordering code;Quantity;Required delivery date
HMI | MANUAL | product_model;document_type | product_model | Product model / ordering code;Document type requested
HMI | DEFECT | product_model;serial_no;error_code;operating_condition;photos;program_backup | serial_no;error_code | Product model / ordering code;Serial number (nameplate);Error code or symptom displayed;Operating condition at failure (load, speed, temperature);Photos of product and nameplate;PLC/HMI project backup
HMI | COMPLIANCE | product_model;target_standard;target_country | target_standard | Product model / ordering code;Required standard / certificate;Destination country / market
HMI | QUOTE | product_model;quantity;incoterms;required_date | quantity;incoterms | Product model / ordering code;Quantity;Incoterms and delivery destination;Required delivery date
HMI | FW_UPDATE | product_model;serial_no;current_fw;tool_version;program_backup | current_fw | Product model / ordering code;Serial number (nameplate);Current firmware version;Engineering tool / loader version;PLC/HMI project backup
HMI | RETURN | purchase_doc;serial_no;return_reason;photos;packaging_condition | purchase_doc;return_reason | PO or invoice number;Serial number (nameplate);Reason for return;Photos of product and nameplate;Packaging condition on arrival
TRANSFORMER | TECH_SPEC | product_model;application | product_model | Product model / ordering code;Application (voltage, load, duty)
TRANSFORMER | INSTALL | product_model;serial_no;site_condition;wiring_diagram | product_model;site_condition | Product model / ordering code;Serial number (nameplate);Site condition (ambient temperature, altitude, humidity);Wiring / single-line diagram
TRANSFORMER | WARRANTY | serial_no;purchase_doc;install_date;failure_description;photos | serial_no;purchase_doc | Serial number (nameplate);PO or invoice number;Installation / commissioning date;Failure description and occurrence time;Photos of product and nameplate
TRANSFORMER | ORDER_LEAD | po_number;product_model;quantity;required_date | po_number | PO number;Product model / ordering code;Quantity;Required delivery date
TRANSFORMER | MANUAL | product_model;document_type | product_model | Product model / ordering code;Document type requested
TRANSFORMER | DEFECT | product_model;serial_no;error_code;operating_condition;photos;load_profile | serial_no;error_code | Product model / ordering code;Serial number (nameplate);Error code or symptom displayed;Operating condition at failure (load, speed, temperature);Photos of product and nameplate;Load current / temperature records
TRANSFORMER | COMPLIANCE | product_model;target_standard;target_country | target_standard | Product model / ordering code;Required standard / certificate;Destination country / market
TRANSFORMER | QUOTE | product_model;quantity;incoterms;required_date | quantity;incoterms | Product model / ordering code;Quantity;Incoterms and delivery destination;Required delivery date
TRANSFORMER | FW_UPDATE | product_model;serial_no;current_fw;tool_version | current_fw | Product model / ordering code;Serial number (nameplate);Current firmware version;Engineering tool / loader version
TRANSFORMER | RETURN | purchase_doc;serial_no;return_reason;photos;packaging_condition | purchase_doc;return_reason | PO or invoice number;Serial number (nameplate);Reason for return;Photos of product and nameplate;Packaging condition on arrival
METER | TECH_SPEC | product_model;application | product_model | Product model / ordering code;Application (voltage, load, duty)
METER | INSTALL | product_model;serial_no;site_condition;wiring_diagram | product_model;site_condition | Product model / ordering code;Serial number (nameplate);Site condition (ambient temperature, altitude, humidity);Wiring / single-line diagram
METER | WARRANTY | serial_no;purchase_doc;install_date;failure_description;photos | serial_no;purchase_doc | Serial number (nameplate);PO or invoice number;Installation / commissioning date;Failure description and occurrence time;Photos of product and nameplate
METER | ORDER_LEAD | po_number;product_model;quantity;required_date | po_number | PO number;Product model / ordering code;Quantity;Required delivery date
METER | MANUAL | product_model;document_type | product_model | Product model / ordering code;Document type requested
METER | DEFECT | product_model;serial_no;error_code;operating_condition;photos | serial_no;error_code | Product model / ordering code;Serial number (nameplate);Error code or symptom displayed;Operating condition at failure (load, speed, temperature);Photos of product and nameplate
METER | COMPLIANCE | product_model;target_standard;target_country | target_standard | Product model / ordering code;Required standard / certificate;Destination country / market
METER | QUOTE | product_model;quantity;incoterms;required_date | quantity;incoterms | Product model / ordering code;Quantity;Incoterms and delivery destination;Required delivery date
METER | FW_UPDATE | product_model;serial_no;current_fw;tool_version | current_fw | Product model / ordering code;Serial number (nameplate);Current firmware version;Engineering tool / loader version
METER | RETURN | purchase_doc;serial_no;return_reason;photos;packaging_condition | purchase_doc;return_reason | PO or invoice number;Serial number (nameplate);Reason for return;Photos of product and nameplate;Packaging condition on arrival
ESS | TECH_SPEC | product_model;application | product_model | Product model / ordering code;Application (voltage, load, duty)
ESS | INSTALL | product_model;serial_no;site_condition;wiring_diagram | product_model;site_condition | Product model / ordering code;Serial number (nameplate);Site condition (ambient temperature, altitude, humidity);Wiring / single-line diagram
ESS | WARRANTY | serial_no;purchase_doc;install_date;failure_description;photos | serial_no;purchase_doc | Serial number (nameplate);PO or invoice number;Installation / commissioning date;Failure description and occurrence time;Photos of product and nameplate
ESS | ORDER_LEAD | po_number;product_model;quantity;required_date | po_number | PO number;Product model / ordering code;Quantity;Required delivery date
ESS | MANUAL | product_model;document_type | product_model | Product model / ordering code;Document type requested
ESS | DEFECT | product_model;serial_no;error_code;operating_condition;photos;logs;battery_status | serial_no;error_code | Product model / ordering code;Serial number (nameplate);Error code or symptom displayed;Operating condition at failure (load, speed, temperature);Photos of product and nameplate;Event / trip log export;Battery SOC / cell temperature at event
ESS | COMPLIANCE | product_model;target_standard;target_country | target_standard | Product model / ordering code;Required standard / certificate;Destination country / market
ESS | QUOTE | product_model;quantity;incoterms;required_date | quantity;incoterms | Product model / ordering code;Quantity;Incoterms and delivery destination;Required delivery date
ESS | FW_UPDATE | product_model;serial_no;current_fw;tool_version;logs | current_fw | Product model / ordering code;Serial number (nameplate);Current firmware version;Engineering tool / loader version;Event / trip log export
ESS | RETURN | purchase_doc;serial_no;return_reason;photos;packaging_condition | purchase_doc;return_reason | PO or invoice number;Serial number (nameplate);Reason for return;Photos of product and nameplate;Packaging condition on arrival
PV | TECH_SPEC | product_model;application | product_model | Product model / ordering code;Application (voltage, load, duty)
PV | INSTALL | product_model;serial_no;site_condition;wiring_diagram;string_config | product_model;site_condition | Product model / ordering code;Serial number (nameplate);Site condition (ambient temperature, altitude, humidity);Wiring / single-line diagram;PV string configuration (modules per string)
PV | WARRANTY | serial_no;purchase_doc;install_date;failure_description;photos | serial_no;purchase_doc | Serial number (nameplate);PO or invoice number;Installation / commissioning date;Failure description and occurrence time;Photos of product and nameplate
PV | ORDER_LEAD | po_number;product_model;quantity;required_date | po_number | PO number;Product model / ordering code;Quantity;Required delivery date
PV | MANUAL | product_model;document_type | product_model | Product model / ordering code;Document type requested
PV | DEFECT | product_model;serial_no;error_code;operating_condition;photos;logs;string_config | serial_no;error_code | Product model / ordering code;Serial number (nameplate);Error code or symptom displayed;Operating condition at failure (load, speed, temperature);Photos of product and nameplate;Event / trip log export;PV string configuration (modules per string)
PV | COMPLIANCE | product_model;target_standard;target_country | target_standard | Product model / ordering code;Required standard / certificate;Destination country / market
PV | QUOTE | product_model;quantity;incoterms;required_date | quantity;incoterms | Product model / ordering code;Quantity;Incoterms and delivery destination;Required delivery date
PV | FW_UPDATE | product_model;serial_no;current_fw;tool_version | current_fw | Product model / ordering code;Serial number (nameplate);Current firmware version;Engineering tool / loader version
PV | RETURN | purchase_doc;serial_no;return_reason;photos;packaging_condition | purchase_doc;return_reason | PO or invoice number;Serial number (nameplate);Reason for return;Photos of product and nameplate;Packaging condition on arrival
UPS | TECH_SPEC | product_model;application | product_model | Product model / ordering code;Application (voltage, load, duty)
UPS | INSTALL | product_model;serial_no;site_condition;wiring_diagram | product_model;site_condition | Product model / ordering code;Serial number (nameplate);Site condition (ambient temperature, altitude, humidity);Wiring / single-line diagram
UPS | WARRANTY | serial_no;purchase_doc;install_date;failure_description;photos | serial_no;purchase_doc | Serial number (nameplate);PO or invoice number;Installation / commissioning date;Failure description and occurrence time;Photos of product and nameplate
UPS | ORDER_LEAD | po_number;product_model;quantity;required_date | po_number | PO number;Product model / ordering code;Quantity;Required delivery date
UPS | MANUAL | product_model;document_type | product_model | Product model / ordering code;Document type requested
UPS | DEFECT | product_model;serial_no;error_code;operating_condition;photos;logs;battery_age | serial_no;error_code | Product model / ordering code;Serial number (nameplate);Error code or symptom displayed;Operating condition at failure (load, speed, temperature);Photos of product and nameplate;Event / trip log export;Battery installation date / age
UPS | COMPLIANCE | product_model;target_standard;target_country | target_standard | Product model / ordering code;Required standard / certificate;Destination country / market
UPS | QUOTE | product_model;quantity;incoterms;required_date | quantity;incoterms | Product model / ordering code;Quantity;Incoterms and delivery destination;Required delivery date
UPS | FW_UPDATE | product_model;serial_no;current_fw;tool_version | current_fw | Product model / ordering code;Serial number (nameplate);Current firmware version;Engineering tool / loader version
UPS | RETURN | purchase_doc;serial_no;return_reason;photos;packaging_condition | purchase_doc;return_reason | PO or invoice number;Serial number (nameplate);Reason for return;Photos of product and nameplate;Packaging condition on arrival

## info_field_codebook
field | label
product_model | Product model / ordering code
serial_no | Serial number (nameplate)
application | Application (voltage, load, duty)
target_standard | Required standard / certificate
target_country | Destination country / market
site_condition | Site condition (ambient temperature, altitude, humidity)
wiring_diagram | Wiring / single-line diagram
photos | Photos of product and nameplate
purchase_doc | PO or invoice number
install_date | Installation / commissioning date
failure_description | Failure description and occurrence time
po_number | PO number
quantity | Quantity
required_date | Required delivery date
incoterms | Incoterms and delivery destination
document_type | Document type requested
doc_language | Preferred document language
error_code | Error code or symptom displayed
operating_condition | Operating condition at failure (load, speed, temperature)
logs | Event / trip log export
current_fw | Current firmware version
tool_version | Engineering tool / loader version
return_reason | Reason for return
packaging_condition | Packaging condition on arrival
parameter_backup | Parameter backup file
motor_nameplate | Motor nameplate data
program_backup | PLC/HMI project backup
battery_status | Battery SOC / cell temperature at event
load_profile | Load current / temperature records
oil_test | Oil test (DGA) report
string_config | PV string configuration (modules per string)
battery_age | Battery installation date / age

## urgency_codebook
urgency | description
SAFETY | 안전 위험 (발연·화재·감전·과열·아크)
SITE_DOWN | 설비/라인 전체 정지
PROD_IMPACT | 생산·운전 영향 또는 반복 트립
COMMISSION | 시운전 일정 차질
DEADLINE | 고객이 명시한 기한(입찰·출하 등) 임박
NONE | 특이사항 없음